## SunSpec_Classic
model_id | model_label | addr_offset | group_offset | name | enum_value | count | type | size | scale_factor | units | rw_access | mandatory | static | label | description | LD | LN | DO | DA | CDC | FC | mms_addr | factor | incompatible | excluded | note
1 | Common | 2 |  | Mn |  |  | string | 16 |  |  |  | M | S | Manufacturer | Well known value registered with SunSpec for compliance | PV | DGEN | EEName | vendor | DPL | DC
1 | Common | 18 |  | Md |  |  | string | 16 |  |  |  | M | S | Model | Manufacturer specific value (32 chars) | PV | DGEN | EEName | model | DPL | DC
1 | Common | 34 |  | Opt |  |  | string | 8 |  |  |  |  | S | Options | Manufacturer specific value (16 chars) | PV | DGEN | EEName | d | DPL | DC
1 | Common | 42 |  | Vr |  |  | string | 8 |  |  |  |  | S | Version | Manufacturer specific value (16 chars) | PV | DGEN | EEName | swRev | DPL | DC
1 | Common | 50 |  | SN |  |  | string | 16 |  |  |  | M | S | Serial Number | Manufacturer specific value (32 chars) | PV | DGEN | EEName | serNum | DPL | DC
10 | Communication Interface Header | 2 |  | St |  |  | enum16 |  |  |  |  | M |  | Interface Status | Overall interface status | [9 empty] | x | communication related parameter, not yet implemented
10 | Communication Interface Header |  |  | DOWN | 0
10 | Communication Interface Header |  |  | UP | 1
10 | Communication Interface Header |  |  | FAULT | 2
10 | Communication Interface Header | 3 |  | Ctl |  |  | uint16 |  |  |  | RW |  |  | Interface Control | Overall interface control (TBD) | [9 empty] | x | communication related parameter, not yet implemented
10 | Communication Interface Header | 4 |  | Typ |  |  | enum16 | [6 empty] | Physical Access Type | Enumerated value. Type of physical media | [9 empty] | x | communication related parameter, not yet implemented
10 | Communication Interface Header |  |  | UNKNOWN | 0
10 | Communication Interface Header |  |  | INTERNAL | 1
10 | Communication Interface Header |  |  | TWISTED_PAIR | 2
10 | Communication Interface Header |  |  | FIBER | 3
10 | Communication Interface Header |  |  | WIRELESS | 4
11 | Ethernet Link Layer | 2 |  | St |  |  | enum16 |  |  |  |  | M |  | Interface Status | Overall interface status | [9 empty] | x | communication related parameter, not yet implemented
11 | Ethernet Link Layer |  |  | DOWN | 0
11 | Ethernet Link Layer |  |  | UP | 1
11 | Ethernet Link Layer |  |  | FAULT | 2
11 | Ethernet Link Layer | 4 |  | Typ |  |  | enum16 | [6 empty] | Physical Access Type | Enumerated value. Type of physical media | [9 empty] | x | communication related parameter, not yet implemented
11 | Ethernet Link Layer |  |  | UNKNOWN | 0
11 | Ethernet Link Layer |  |  | INTERNAL | 1
11 | Ethernet Link Layer |  |  | TWISTED_PAIR | 2
11 | Ethernet Link Layer |  |  | FIBER | 3
11 | Ethernet Link Layer |  |  | WIRELESS | 4
11 | Ethernet Link Layer | 5 |  | Pad |  |  | pad | [17 empty] | x | no matching required
103 | Inverter (Three Phase) | 0 |  | ID | 103 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier | [9 empty] | x | no matching required
103 | Inverter (Three Phase) | 1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length | [9 empty] | x | no matching required
103 | Inverter (Three Phase) | 2 |  | A |  |  | uint16 |  | A_SF | A |  | M |  | Amps | AC Current | PV | MMXU | A | res.cVal.mag.f | WYE | MX
103 | Inverter (Three Phase) | 3 |  | AphA |  |  | uint16 |  | A_SF | A |  | M |  | Amps PhaseA | Phase A Current | PV | MMXU | A | phsA.cVal.mag.f | WYE | MX
103 | Inverter (Three Phase) | 4 |  | AphB |  |  | uint16 |  | A_SF | A |  | M |  | Amps PhaseB | Phase B Current | PV | MMXU | A | phsB.cVal.mag.f | WYE | MX
103 | Inverter (Three Phase) | 5 |  | AphC |  |  | uint16 |  | A_SF | A |  | M |  | Amps PhaseC | Phase C Current | PV | MMXU | A | phsC.cVal.mag.f | WYE | MX
103 | Inverter (Three Phase) | 6 |  | A_SF |  |  | sunssf |  |  |  |  | M | [12 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
103 | Inverter (Three Phase) | 7 |  | PPVphAB |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage AB | Phase Voltage AB | PV | MMXU | PPV | phsAB.cVal.mag.f | DEL | MX
103 | Inverter (Three Phase) | 8 |  | PPVphBC |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage BC | Phase Voltage BC | PV | MMXU | PPV | phsBC.cVal.mag.f | DEL | MX
103 | Inverter (Three Phase) | 9 |  | PPVphCA |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage CA | Phase Voltage CA | PV | MMXU | PPV | phsCA.cVal.mag.f | DEL | MX
103 | Inverter (Three Phase) | 10 |  | PhVphA |  |  | uint16 |  | V_SF | V |  | M |  | Phase Voltage AN | Phase Voltage AN | PV | MMXU | PhV | phsA.cVal.mag.f | WYE | MX
103 | Inverter (Three Phase) | 11 |  | PhVphB |  |  | uint16 |  | V_SF | V |  | M |  | Phase Voltage BN | Phase Voltage BN | PV | MMXU | PhV | phsB.cVal.mag.f | WYE | MX
103 | Inverter (Three Phase) | 12 |  | PhVphC |  |  | uint16 |  | V_SF | V |  | M |  | Phase Voltage CN | Phase Voltage CN | PV | MMXU | PhV | phsC.cVal.mag.f | WYE | MX
103 | Inverter (Three Phase) | 13 |  | V_SF |  |  | sunssf |  |  |  |  | M | [12 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
103 | Inverter (Three Phase) | 14 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | AC Power | PV | MMXU | TotW | mag.f | MV | MX
103 | Inverter (Three Phase) | 15 |  | W_SF |  |  | sunssf |  |  |  |  | M | [12 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
103 | Inverter (Three Phase) | 16 |  | Hz |  |  | uint16 |  | Hz_SF | Hz |  | M |  | Hz | Line Frequency | PV | MMXU | Hz | mag.f | MV | MX
103 | Inverter (Three Phase) | 17 |  | Hz_SF |  |  | sunssf |  |  |  |  | M | [12 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
103 | Inverter (Three Phase) | 18 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power | PV | MMXU | TotVA | mag.f | MV | MX
103 | Inverter (Three Phase) | 19 |  | VA_SF |  |  | sunssf | [17 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
103 | Inverter (Three Phase) | 20 |  | VAr |  |  | int16 |  | VAr_SF | var |  |  |  | VAr | AC Reactive Power | PV | MMXU | TotVAr | mag.f | MV | MX
103 | Inverter (Three Phase) | 21 |  | VAr_SF |  |  | sunssf | [17 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
103 | Inverter (Three Phase) | 22 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | AC Power Factor | PV | MMXU | PF | mag.f | MV | MX
103 | Inverter (Three Phase) | 23 |  | PF_SF |  |  | sunssf | [17 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
103 | Inverter (Three Phase) | 24 |  | WH |  |  | acc32 |  | WH_SF | Wh |  | M |  | WattHours | AC Energy | PV | DGEN | GnEnPer | mag.f | MV | MX
103 | Inverter (Three Phase) | 26 |  | WH_SF |  |  | sunssf |  |  |  |  | M | [12 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
103 | Inverter (Three Phase) | 27 |  | DCA |  |  | uint16 |  | DCA_SF | A |  |  |  | DC Amps | DC Current | [9 empty] | x | DC side parameters (LN: DBAT) are not implemented in the IEC 61850 data model
103 | Inverter (Three Phase) | 28 |  | DCA_SF |  |  | sunssf | [17 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
103 | Inverter (Three Phase) | 29 |  | DCV |  |  | uint16 |  | DCV_SF | V |  |  |  | DC Voltage | DC Voltage | [9 empty] | x | DC side parameters (LN: DBAT) are not implemented in the IEC 61850 data model
103 | Inverter (Three Phase) | 30 |  | DCV_SF |  |  | sunssf | [17 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
103 | Inverter (Three Phase) | 31 |  | DCW |  |  | int16 |  | DCW_SF | W |  |  |  | DC Watts | DC Power | [9 empty] | x | DC side parameters (LN: DBAT) are not implemented in the IEC 61850 data model
103 | Inverter (Three Phase) | 32 |  | DCW_SF |  |  | sunssf | [17 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
103 | Inverter (Three Phase) | 33 |  | TmpCab |  |  | int16 |  | Tmp_SF | C |  | M |  | Cabinet Temperature | Cabinet Temperature | [9 empty] | x | Environmental parameters (LN: XXXX) are not implemented in the IEC 61850 data model
103 | Inverter (Three Phase) | 34 |  | TmpSnk |  |  | int16 |  | Tmp_SF | C |  |  |  | Heat Sink Temperature | Heat Sink Temperature | [9 empty] | x | Environmental parameters (LN: XXXX) are not implemented in the IEC 61850 data model
103 | Inverter (Three Phase) | 35 |  | TmpTrns |  |  | int16 |  | Tmp_SF | C |  |  |  | Transformer Temperature | Transformer Temperature | [9 empty] | x | Environmental parameters (LN: XXXX) are not implemented in the IEC 61850 data model
103 | Inverter (Three Phase) | 36 |  | TmpOt |  |  | int16 |  | Tmp_SF | C |  |  |  | Other Temperature | Other Temperature | [9 empty] | x | Environmental parameters (LN: XXXX) are not implemented in the IEC 61850 data model
103 | Inverter (Three Phase) | 37 |  | Tmp_SF |  |  | sunssf |  |  |  |  | M | [12 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
103 | Inverter (Three Phase) | 38 |  | St |  |  | enum16 |  |  |  |  | M |  | Operating State | Enumerated value. Operating state | [8 empty] | x | x | incompatible with IEC 61850 DO DEROpSt
103 | Inverter (Three Phase) |  |  | OFF | 1
103 | Inverter (Three Phase) |  |  | SLEEPING | 2
103 | Inverter (Three Phase) |  |  | STARTING | 3
103 | Inverter (Three Phase) |  |  | MPPT | 4
103 | Inverter (Three Phase) |  |  | THROTTLED | 5
103 | Inverter (Three Phase) |  |  | SHUTTING_DOWN | 6
103 | Inverter (Three Phase) |  |  | FAULT | 7
103 | Inverter (Three Phase) |  |  | STANDBY | 8
103 | Inverter (Three Phase) | 39 |  | StVnd |  |  | enum16 | [6 empty] | Vendor Operating State | Vendor specific operating state code | [8 empty] | x | x | incompatible with IEC 61850 DO DEROpSt
103 | Inverter (Three Phase) | 40 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Event1 | Bitmask value. Event fields | [9 empty] | x | Event parameters (LN: XXXX) are not implemented in the IEC 61850 data model
103 | Inverter (Three Phase) |  |  | GROUND_FAULT | 0
103 | Inverter (Three Phase) |  |  | DC_OVER_VOLT | 1
103 | Inverter (Three Phase) |  |  | AC_DISCONNECT | 2
103 | Inverter (Three Phase) |  |  | DC_DISCONNECT | 3
103 | Inverter (Three Phase) |  |  | GRID_DISCONNECT | 4
103 | Inverter (Three Phase) |  |  | CABINET_OPEN | 5
103 | Inverter (Three Phase) |  |  | MANUAL_SHUTDOWN | 6
103 | Inverter (Three Phase) |  |  | OVER_TEMP | 7
103 | Inverter (Three Phase) |  |  | OVER_FREQUENCY | 8
103 | Inverter (Three Phase) |  |  | UNDER_FREQUENCY | 9
103 | Inverter (Three Phase) |  |  | AC_OVER_VOLT | 10
103 | Inverter (Three Phase) |  |  | AC_UNDER_VOLT | 11
103 | Inverter (Three Phase) |  |  | BLOWN_STRING_FUSE | 12
103 | Inverter (Three Phase) |  |  | UNDER_TEMP | 13
103 | Inverter (Three Phase) |  |  | MEMORY_LOSS | 14
103 | Inverter (Three Phase) |  |  | HW_TEST_FAILURE | 15
103 | Inverter (Three Phase) | 42 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Event Bitfield 2 | Reserved for future use | [9 empty] | x | Event parameters (LN: XXXX) are not implemented in the IEC 61850 data model
103 | Inverter (Three Phase) | 44 |  | EvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 1 | Vendor defined events | [9 empty] | x | Event parameters (LN: XXXX) are not implemented in the IEC 61850 data model
103 | Inverter (Three Phase) | 46 |  | EvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 2 | Vendor defined events | [9 empty] | x | Event parameters (LN: XXXX) are not implemented in the IEC 61850 data model
103 | Inverter (Three Phase) | 48 |  | EvtVnd3 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 3 | Vendor defined events | [9 empty] | x | Event parameters (LN: XXXX) are not implemented in the IEC 61850 data model
103 | Inverter (Three Phase) | 50 |  | EvtVnd4 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 4 | Vendor defined events | [9 empty] | x | Event parameters (LN: XXXX) are not implemented in the IEC 61850 data model
120 | Nameplate | 0 |  | ID | 120 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier | [9 empty] | x | no matching required
120 | Nameplate | 1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length | [9 empty] | x | no matching required
120 | Nameplate | 2 |  | DERTyp |  |  | enum16 |  |  |  |  | M |  | DERTyp | Type of DER device. Default value is 4 to indicate PV device. | [8 empty] | x | x | incompatible with IEC 61850 DO DERTyp
120 | Nameplate |  |  | PV | 4
120 | Nameplate |  |  | PV_STOR | 82
120 | Nameplate | 3 |  | WRtg |  |  | uint16 |  | WRtg_SF | W |  | M |  | WRtg | Continuous power output capability of the inverter. | PV | DGEN | WMaxRtg | setMag.f | ASG | SP |  |  |  |  | alternative DINV.WRtg.setMag.f
120 | Nameplate | 4 |  | WRtg_SF |  |  | sunssf |  |  |  |  | M |  | WRtg_SF | Scale factor | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
120 | Nameplate | 5 |  | VARtg |  |  | uint16 |  | VARtg_SF | VA |  | M |  | VARtg | Continuous Volt-Ampere capability of the inverter. | PV | DGEN | VAMaxRtg | setMag.f | ASG | SP |  |  |  |  | alternative DINV.VARtg.setMag.f
120 | Nameplate | 6 |  | VARtg_SF |  |  | sunssf |  |  |  |  | M |  | VARtg_SF | Scale factor | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
120 | Nameplate | 7 |  | VArRtgQ1 |  |  | int16 |  | VArRtg_SF | var |  | M |  | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1. | PV | DGEN | IvarMaxRtg | setMag.f | ASG | SP |  |  | x |  | LN DGEN of IEC61850 only distinguishes between absorbing and injection
120 | Nameplate | 8 |  | VArRtgQ2 |  |  | int16 |  | VArRtg_SF | var |  | M |  | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2. | PV | DGEN | IvarMaxRtg | setMag.f | ASG | SP |  |  | x |  | LN DGEN of IEC61850 only distinguishes between absorbing and injection
120 | Nameplate | 9 |  | VArRtgQ3 |  |  | int16 |  | VArRtg_SF | var |  | M |  | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3. | PV | DGEN | AvarMaxRtg | setMag.f | ASG | SP |  |  | x |  | LN DGEN of IEC61850 only distinguishes between absorbing and injection
120 | Nameplate | 10 |  | VArRtgQ4 |  |  | int16 |  | VArRtg_SF | var |  | M |  | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4. | PV | DGEN | AvarMaxRtg | setMag.f | ASG | SP |  |  | x |  | LN DGEN of IEC61850 only distinguishes between absorbing and injection
120 | Nameplate | 11 |  | VArRtg_SF |  |  | sunssf |  |  |  |  | M |  | VArRtg_SF | Scale factor | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
120 | Nameplate | 12 |  | ARtg |  |  | uint16 |  | ARtg_SF | A |  | M |  | ARtg | Maximum RMS AC current level capability of the inverter. | PV | DGEN | AMaxRtg | setMag.f | ASG | SP
120 | Nameplate | 13 |  | ARtg_SF |  |  | sunssf |  |  |  |  | M |  | ARtg_SF | Scale factor | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
120 | Nameplate | 14 |  | PFRtgQ1 |  |  | int16 |  | PFRtg_SF | cos() |  | M |  | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | PV | DGEN | OvPFRtg | setMag.f | ASG | SP |  |  |  |  | Parameters related to reactive power service are not yet implemented in our IEC 61850 data model.
120 | Nameplate | 15 |  | PFRtgQ2 |  |  | int16 |  | PFRtg_SF | cos() |  | M |  | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | PV | DGEN | OvPFRtg | setMag.f | ASG | SP |  |  |  |  | Parameters related to reactive power service are not yet implemented in our IEC 61850 data model.
120 | Nameplate | 16 |  | PFRtgQ3 |  |  | int16 |  | PFRtg_SF | cos() |  | M |  | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | PV | DGEN | UnPFRtg | setMag.f | ASG | SP |  |  |  |  | Parameters related to reactive power service are not yet implemented in our IEC 61850 data model.
120 | Nameplate | 17 |  | PFRtgQ4 |  |  | int16 |  | PFRtg_SF | cos() |  | M |  | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | PV | DGEN | UnPFRtg | setMag.f | ASG | SP |  |  |  |  | Parameters related to reactive power service are not yet implemented in our IEC 61850 data model.
120 | Nameplate | 18 |  | PFRtg_SF |  |  | sunssf |  |  |  |  | M |  | PFRtg_SF | Scale factor | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
120 | Nameplate | 19 |  | WHRtg |  |  | uint16 |  | WHRtg_SF | Wh |  |  |  | WHRtg | Nominal energy rating of storage device. | STO | DSTO | WhRtg | setMag.f | ASG | SP
120 | Nameplate | 20 |  | WHRtg_SF |  |  | sunssf | [6 empty] | WHRtg_SF | Scale factor | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
120 | Nameplate | 21 |  | AhrRtg |  |  | uint16 |  | AhrRtg_SF | AH |  |  |  | AhrRtg | The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). | [8 empty] | x | x | not available in IEC 61850?
120 | Nameplate | 22 |  | AhrRtg_SF |  |  | sunssf | [6 empty] | AhrRtg_SF | Scale factor for amp-hour rating. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
120 | Nameplate | 23 |  | MaxChaRte |  |  | uint16 |  | MaxChaRte_SF | W |  |  |  | MaxChaRte | Maximum rate of energy transfer into the storage device. | STO | DSTO | ChaWMaxRtg | setMag.f | ASG | SP |  |  |  |  | Charging rate is uderstood as charing power here, when it comes to the battery settings.
120 | Nameplate | 24 |  | MaxChaRte_SF |  |  | sunssf | [6 empty] | MaxChaRte_SF | Scale factor | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
120 | Nameplate | 25 |  | MaxDisChaRte |  |  | uint16 |  | MaxDisChaRte_SF | W |  |  |  | MaxDisChaRte | Maximum rate of energy transfer out of the storage device. | STO | DSTO | DschWMaxRtg | setMag.f | ASG | SP |  |  |  |  | Charging rate is uderstood as charing power here, when it comes to the battery settings.
120 | Nameplate | 26 |  | MaxDisChaRte_SF |  |  | sunssf | [6 empty] | MaxDisChaRte_SF | Scale factor | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
120 | Nameplate | 27 |  | Pad |  |  | pad | [6 empty] | Pad | Pad register. | [9 empty] | x | no matching required
121 | Basic Settings | 0 |  | ID | 121 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier | [9 empty] | x | no matching required
121 | Basic Settings | 1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length | [9 empty] | x | no matching required
121 | Basic Settings | 2 |  | WMax |  |  | uint16 |  | WMax_SF | W | RW | M |  | WMax | Setting for maximum power output. Default to WRtg. | PV | DGEN | WMax | setMag.f | ASG | SP
121 | Basic Settings | 3 |  | VRef |  |  | uint16 |  | VRef_SF | V | RW | M |  | VRef | Voltage at the PCC. | PV | DECP | Vref | setMag.f | ASG | SP
121 | Basic Settings | 4 |  | VRefOfs |  |  | int16 |  | VRefOfs_SF | V | RW | M |  | VRefOfs | Offset from PCC to inverter. | [9 empty] | x | not available in IEC 61850?
121 | Basic Settings | 5 |  | VMax |  |  | uint16 |  | VMinMax_SF | V | RW |  |  | VMax | Setpoint for maximum voltage. | PV | DGEN | VMaxRtg | setMag.f | ASG | SP
121 | Basic Settings | 6 |  | VMin |  |  | uint16 |  | VMinMax_SF | V | RW |  |  | VMin | Setpoint for minimum voltage. | PV | DGEN | VMinRtg | setMag.f | ASG | SP
121 | Basic Settings | 7 |  | VAMax |  |  | uint16 |  | VAMax_SF | VA | RW |  |  | VAMax | Setpoint for maximum apparent power. Default to VARtg. | PV | DGEN | VAMax | setMag.f | ASG | SP
121 | Basic Settings | 8 |  | VArMaxQ1 |  |  | int16 |  | VArMax_SF | var | RW |  |  | VArMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | PV | DGEN | IvarMax | setMag.f | ASG | SP |  |  |  |  | LN DGEN of IEC61850 only distinguishes between absorbing and injection
121 | Basic Settings | 9 |  | VArMaxQ2 |  |  | int16 |  | VArMax_SF | var | RW |  |  | VArMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | PV | DGEN | IvarMax | setMag.f | ASG | SP |  |  |  |  | LN DGEN of IEC61850 only distinguishes between absorbing and injection
121 | Basic Settings | 10 |  | VArMaxQ3 |  |  | int16 |  | VArMax_SF | var | RW |  |  | VArMaxQ3 | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. | PV | DGEN | AvarMax | setMag.f | ASG | SP |  |  |  |  | LN DGEN of IEC61850 only distinguishes between absorbing and injection
121 | Basic Settings | 11 |  | VArMaxQ4 |  |  | int16 |  | VArMax_SF | var | RW |  |  | VArMaxQ4 | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. | PV | DGEN | AvarMax | setMag.f | ASG | SP |  |  |  |  | LN DGEN of IEC61850 only distinguishes between absorbing and injection
121 | Basic Settings | 12 |  | WGra |  |  | uint16 |  | WGra_SF | % WMax/sec | RW |  |  | WGra | Default ramp rate of change of active power due to command or internal action. | PV | DGEN | WRmp | setMag.f | ASG | SP
121 | Basic Settings | 13 |  | PFMinQ1 |  |  | int16 |  | PFMin_SF | cos() | RW |  |  | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | [9 empty] | x | LN DGEN of IEC61850 only defines maximum PF value
121 | Basic Settings | 14 |  | PFMinQ2 |  |  | int16 |  | PFMin_SF | cos() | RW |  |  | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | [9 empty] | x | LN DGEN of IEC61850 only defines maximum PF value
121 | Basic Settings | 15 |  | PFMinQ3 |  |  | int16 |  | PFMin_SF | cos() | RW |  |  | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | [9 empty] | x | LN DGEN of IEC61850 only defines maximum PF value
121 | Basic Settings | 16 |  | PFMinQ4 |  |  | int16 |  | PFMin_SF | cos() | RW |  |  | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | [9 empty] | x | LN DGEN of IEC61850 only defines maximum PF value
121 | Basic Settings | 17 |  | VArAct |  |  | enum16 |  |  |  | RW |  |  | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. | [8 empty] | x | x | not available in IEC 61850?
121 | Basic Settings |  |  | SWITCH | 1
121 | Basic Settings |  |  | MAINTAIN | 2
121 | Basic Settings | 18 |  | ClcTotVA |  |  | enum16 |  |  |  | RW |  |  | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic. | [9 empty] | x | statistic parameters are not yet implemented in our IEC 61850 data model
121 | Basic Settings |  |  | VECTOR | 1
121 | Basic Settings |  |  | ARITHMETIC | 2
121 | Basic Settings | 19 |  | MaxRmpRte |  |  | uint16 |  | MaxRmpRte_SF | % WGra | RW |  |  | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. | [9 empty] | x | which one is exactly nominal maximum ramp rate?
121 | Basic Settings | 20 |  | ECPNomHz |  |  | uint16 |  | ECPNomHz_SF | Hz | RW |  |  | ECPNomHz | Setpoint for nominal frequency at the ECP. | PV | DECP | HzNom | setMag.f | ASG | SP
121 | Basic Settings | 21 |  | ConnPh |  |  | enum16 |  |  |  | RW |  |  | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3. | PV | DECP | PhsConnTyp | stVal.f | ENS | ST |  |  | x |  | the IEC 61850 DO is of type enumeration!
122 | Measurements_Status | 0 |  | ID | 122 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier | [9 empty] | x | no matching required
122 | Measurements_Status | 1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length | [9 empty] | x | no matching required
122 | Measurements_Status | 2 |  | PVConn |  |  | bitfield16 |  |  |  |  | M |  | PVConn | PV inverter present/available status. Enumerated value. | PV | DGEN | DEROpSt | stVal.f | ENS | ST |  |  | x | x | incompatible enumeration
122 | Measurements_Status |  |  | CONNECTED | 0
122 | Measurements_Status |  |  | AVAILABLE | 1
122 | Measurements_Status |  |  | OPERATING | 2
122 | Measurements_Status |  |  | TEST | 3
122 | Measurements_Status | 3 |  | StorConn |  |  | bitfield16 |  |  |  |  | M |  | StorConn | Storage inverter present/available status. Enumerated value. | STO | DSTO | DEROpSt | stVal.f | ENS | ST |  |  | x | x | incompatible enumeration
122 | Measurements_Status |  |  | CONNECTED | 0
122 | Measurements_Status |  |  | AVAILABLE | 1
122 | Measurements_Status |  |  | OPERATING | 2
122 | Measurements_Status |  |  | TEST | 3
122 | Measurements_Status | 4 |  | ECPConn |  |  | bitfield16 |  |  |  |  | M |  | ECPConn | ECP connection status: disconnected=0 connected=1. | [9 empty] | x | neither DECP nor DPCC records ECP connection status
122 | Measurements_Status |  |  | CONNECTED | 0
122 | Measurements_Status | 5 |  | ActWh |  |  | acc64 |  |  | Wh |  |  |  | ActWh | AC lifetime active (real) energy output. | PV | DGEN | GnEnTot | mag.f | MV | MX
122 | Measurements_Status | 9 |  | ActVAh |  |  | acc64 |  |  | VAh |  |  |  | ActVAh | AC lifetime apparent energy output. | [9 empty] | x | not available in IEC 61850, but can be calculated
122 | Measurements_Status | 13 |  | ActVArhQ1 |  |  | acc64 |  |  | varh |  |  |  | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1. | PV | DGEN | IvarTot | mag.f | MV | MX |  |  |  |  | LN DGEN of IEC61850 only distinguishes between absorbing and injection
122 | Measurements_Status | 17 |  | ActVArhQ2 |  |  | acc64 |  |  | varh |  |  |  | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2. | PV | DGEN | IvarTot | mag.f | MV | MX |  |  |  |  | LN DGEN of IEC61850 only distinguishes between absorbing and injection
122 | Measurements_Status | 21 |  | ActVArhQ3 |  |  | acc64 |  |  | varh |  |  |  | ActVArhQ3 | AC lifetime negative energy output in quadrant 3. | PV | DGEN | AvarTot | mag.f | MV | MX |  |  |  |  | LN DGEN of IEC61850 only distinguishes between absorbing and injection
122 | Measurements_Status | 25 |  | ActVArhQ4 |  |  | acc64 |  |  | varh |  |  |  | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4. | PV | DGEN | AvarTot | mag.f | MV | MX |  |  |  |  | LN DGEN of IEC61850 only distinguishes between absorbing and injection
122 | Measurements_Status | 29 |  | VArAval |  |  | int16 |  | VArAval_SF | var |  |  |  | VArAval | Amount of VARs available without impacting watts output. | PV | DGEN | AvarAvl | mag.f | MV | MX
122 | Measurements_Status | 30 |  | VArAval_SF |  |  | sunssf | [6 empty] | VArAval_SF | Scale factor for available VARs. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
122 | Measurements_Status | 31 |  | WAval |  |  | uint16 |  | WAval_SF | var |  |  |  | WAval | Amount of Watts available. | PV | DGEN | AvlUpW | mag.f | MV | MX |  |  | x |  | there is also AvlDnW, use minus to represent available down W?
122 | Measurements_Status | 32 |  | WAval_SF |  |  | sunssf | [6 empty] | WAval_SF | Scale factor for available Watts. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
122 | Measurements_Status | 33 |  | StSetLimMsk |  |  | bitfield32 | [6 empty] | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. | [9 empty] | x | this parameter is currently not considered in our IEC 61850 data model
122 | Measurements_Status |  |  | WMax | 0
122 | Measurements_Status |  |  | VAMax | 1
122 | Measurements_Status |  |  | VArAval | 2
122 | Measurements_Status |  |  | VArMaxQ1 | 3
122 | Measurements_Status |  |  | VArMaxQ2 | 4
122 | Measurements_Status |  |  | VArMaxQ3 | 5
122 | Measurements_Status |  |  | VArMaxQ4 | 6
122 | Measurements_Status |  |  | PFMinQ1 | 7
122 | Measurements_Status |  |  | PFMinQ2 | 8
122 | Measurements_Status |  |  | PFMinQ3 | 9
122 | Measurements_Status |  |  | PFMinQ4 | 10
122 | Measurements_Status | 35 |  | StActCtl |  |  | bitfield32 | [6 empty] | StActCtl | Bit Mask indicating which inverter controls are currently active. | [9 empty] | x | A very important functional parameter, but currently this is not implemented in our IEC61850 data model.
122 | Measurements_Status |  |  | FixedW | 0
122 | Measurements_Status |  |  | FixedVAR | 1
122 | Measurements_Status |  |  | FixedPF | 2
122 | Measurements_Status |  |  | Volt-VAr | 3
122 | Measurements_Status |  |  | Freq-Watt-Param | 4
122 | Measurements_Status |  |  | Freq-Watt-Curve | 5
122 | Measurements_Status |  |  | Dyn-Reactive-Current | 6
122 | Measurements_Status |  |  | LVRT | 7
122 | Measurements_Status |  |  | HVRT | 8
122 | Measurements_Status |  |  | Watt-PF | 9
122 | Measurements_Status |  |  | Volt-Watt | 10
122 | Measurements_Status |  |  | Scheduled | 12
122 | Measurements_Status |  |  | LFRT | 13
122 | Measurements_Status |  |  | HFRT | 14
122 | Measurements_Status | 37 |  | TmSrc |  |  | string | 4 | [5 empty] | TmSrc | Source of time synchronization. | [9 empty] | x | time synchronization currently not implemented in our IEC61850 data model.
122 | Measurements_Status | 41 |  | Tms |  |  | uint32 |  |  | Secs |  |  |  | Tms | Seconds since 01-01-2000 00:00 UTC | [9 empty] | x | time synchronization currently not implemented in our IEC61850 data model.
122 | Measurements_Status | 43 |  | RtSt |  |  | bitfield16 | [6 empty] | RtSt | Bit Mask indicating active ride-through status. | [9 empty] | x | A very important functional parameter, but currently this is not implemented in our IEC61850 data model.
122 | Measurements_Status |  |  | LVRT_ACTIVE | 0
122 | Measurements_Status |  |  | HVRT_ACTIVE | 1
122 | Measurements_Status |  |  | LFRT_ACTIVE | 2
122 | Measurements_Status |  |  | HFRT_ACTIVE | 3
122 | Measurements_Status | 44 |  | Ris |  |  | uint16 |  | Ris_SF | ohms |  |  |  | Ris | Isolation resistance. | PV | DGEN | GndRisRtg | setMag.f | ASG | SP
122 | Measurements_Status | 45 |  | Ris_SF |  |  | sunssf | [6 empty] | Ris_SF | Scale factor for isolation resistance. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
123 | Immediate Controls | 0 |  | ID | 123 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier | [9 empty] | x | no matching required
123 | Immediate Controls | 1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length | [9 empty] | x | no matching required
123 | Immediate Controls | 2 |  | Conn_WinTms |  |  | uint16 |  |  | Secs | RW |  |  | Conn_WinTms | Time window for connect/disconnect. | [9 empty] | x | Time management parameters are not implemented in our IEC61850 data model.
123 | Immediate Controls | 3 |  | Conn_RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | Conn_RvrtTms | Timeout period for connect/disconnect. | [9 empty] | x | Time management parameters are not implemented in our IEC61850 data model.
123 | Immediate Controls | 4 |  | Conn |  |  | enum16 |  |  |  | RW | M |  | Conn | Enumerated valued. Connection control. | [8 empty] | x | x | this will be determined by checking the connection to PV inverter
123 | Immediate Controls |  |  | DISCONNECT | 0
123 | Immediate Controls |  |  | CONNECT | 1
123 | Immediate Controls | 5 |  | WMaxLimPct |  |  | uint16 |  | WMaxLimPct_SF | % WMax | RW | M |  | WMaxLimPct | Set power output to specified level. | PV | DGEN | OutWSet | setMag.f | ASG | SP |  | 0.01 | x |  | This should be replaced by DGEN.WSpt.ctlVal, as soon as it is properly supported in libiec61850
123 | Immediate Controls | 6 |  | WMaxLimPct_WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WMaxLimPct_WinTms | Time window for power limit change. | [9 empty] | x | currently not considered in our IEC 61850 data model
123 | Immediate Controls | 7 |  | WMaxLimPct_RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | WMaxLimPct_RvrtTms | Timeout period for power limit. | [9 empty] | x | currently not considered in our IEC 61850 data model
123 | Immediate Controls | 8 |  | WMaxLimPct_RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | [9 empty] | x | currently not considered in our IEC 61850 data model
123 | Immediate Controls | 9 |  | WMaxLim_Ena |  |  | enum16 |  |  |  | RW | M |  | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control. | [9 empty] | x | currently not considered in our IEC 61850 data model
123 | Immediate Controls |  |  | DISABLED | 0
123 | Immediate Controls |  |  | ENABLED | 1
123 | Immediate Controls | 10 |  | OutPFSet |  |  | int16 |  | OutPFSet_SF | cos() | RW | M |  | OutPFSet | Set power factor to specific value - cosine of angle. | PV | DGEN | OvPF | setMag.f | ASG | SP
123 | Immediate Controls | 11 |  | OutPFSet_WinTms |  |  | uint16 |  |  | Secs | RW |  |  | OutPFSet_WinTms | Time window for power factor change. | [9 empty] | x | currently not considered in our IEC 61850 data model
123 | Immediate Controls | 12 |  | OutPFSet_RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | OutPFSet_RvrtTms | Timeout period for power factor. | [9 empty] | x | currently not considered in our IEC 61850 data model
123 | Immediate Controls | 13 |  | OutPFSet_RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint. | [9 empty] | x | currently not considered in our IEC 61850 data model
123 | Immediate Controls | 14 |  | OutPFSet_Ena |  |  | enum16 |  |  |  | RW | M |  | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control. | [9 empty] | x | currently not considered in our IEC 61850 data model
123 | Immediate Controls |  |  | DISABLED | 0
123 | Immediate Controls |  |  | ENABLED | 1
123 | Immediate Controls | 15 |  | VArWMaxPct |  |  | int16 |  | VArPct_SF | % WMax | RW |  |  | VArWMaxPct | Reactive power in percent of WMax. | PV | DGEN | VArMax | setMag.f | ASG | SP |  | 0.01 |  |  | In IEC 61850, setting VArMax is not done by percentage, but direct by passing a ASG value.
123 | Immediate Controls | 16 |  | VArMaxPct |  |  | int16 |  | VArPct_SF | % VArMax | RW |  |  | VArMaxPct | Reactive power in percent of VArMax. | PV | DGEN | VArMax | setMag.f | ASG | SP |  | 0.01 |  |  | In IEC 61850, setting VArMax is not done by percentage, but direct by passing a ASG value.
123 | Immediate Controls | 17 |  | VArAvalPct |  |  | int16 |  | VArPct_SF | % VArAval | RW |  |  | VArAvalPct | Reactive power in percent of VArAval. | PV | DGEN | VArMax | setMag.f | ASG | SP |  | 0.01 |  |  | In IEC 61850, setting VArMax is not done by percentage, but direct by passing a ASG value.
123 | Immediate Controls | 18 |  | VArPct_WinTms |  |  | uint16 |  |  | Secs | RW |  |  | VArPct_WinTms | Time window for VAR limit change. | [9 empty] | x | currently not considered in our IEC 61850 data model
123 | Immediate Controls | 19 |  | VArPct_RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | VArPct_RvrtTms | Timeout period for VAR limit. | [9 empty] | x | currently not considered in our IEC 61850 data model
123 | Immediate Controls | 20 |  | VArPct_RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | [9 empty] | x | currently not considered in our IEC 61850 data model
123 | Immediate Controls | 21 |  | VArPct_Mod |  |  | enum16 |  |  |  | RW |  |  | VArPct_Mod | Enumerated value. VAR percent limit mode. | PV | DGEN | VArSptRef | setMag.f | ASG | SP |  |  | x |  | None has the literal 0 in IEC 61850
123 | Immediate Controls |  |  | NONE | 0
123 | Immediate Controls |  |  | WMax | 1
123 | Immediate Controls |  |  | VArMax | 2
123 | Immediate Controls |  |  | VArAval | 3
123 | Immediate Controls | 22 |  | VArPct_Ena |  |  | enum16 |  |  |  | RW | M |  | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control. | [9 empty] | x | currently not considered in our IEC 61850 data model
123 | Immediate Controls |  |  | DISABLED | 0
123 | Immediate Controls |  |  | ENABLED | 1
123 | Immediate Controls | 23 |  | WMaxLimPct_SF |  |  | sunssf |  |  |  |  | M |  | WMaxLimPct_SF | Scale factor for power output percent. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
123 | Immediate Controls | 24 |  | OutPFSet_SF |  |  | sunssf |  |  |  |  | M |  | OutPFSet_SF | Scale factor for power factor. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
123 | Immediate Controls | 25 |  | VArPct_SF |  |  | sunssf | [6 empty] | VArPct_SF | Scale factor for reactive power percent. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
124 | Storage | 0 |  | ID | 124 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier | [9 empty] | x | no matching required
124 | Storage | 1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length | [9 empty] | x | no matching required
124 | Storage | 2 |  | WChaMax |  |  | uint16 |  | WChaMax_SF | W | RW | M |  | WChaMax | Setpoint for maximum charge. | STO | DSTO | ChaWMax | setMag.f | ASG | SP |  |  |  |  | This value should be used as reference for WChaGra and WDisChaGra
124 | Storage | 3 |  | WChaGra |  |  | uint16 |  | WChaDisChaGra_SF | % WChaMax/sec | RW | M |  | WChaGra | Setpoint for maximum charging rate. Default is MaxChaRte. | STO | DSTO | ChaWMax | setMag.f | ASG | SP |  |  |  |  | Charging rate is uderstood as charing power here, when it comes to the battery settings. Only read this parameter if WChaMax is not availlabe
124 | Storage | 4 |  | WDisChaGra |  |  | uint16 |  | WChaDisChaGra_SF | % WChaMax/sec | RW | M |  | WDisChaGra | Setpoint for maximum discharge rate. Default is MaxDisChaRte. | STO | DSTO | DschWMax | setMag.f | ASG | SP |  |  |  |  | Charging rate is uderstood as charing power here, when it comes to the battery settings.
124 | Storage | 5 |  | StorCtl_Mod |  |  | bitfield16 |  |  |  | RW | M |  | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value. | [9 empty] | x | currently not considered in our IEC 61850 data model
124 | Storage |  |  | CHARGE | 0
124 | Storage |  |  | DiSCHARGE | 1
124 | Storage | 6 |  | VAChaMax |  |  | uint16 |  | VAChaMax_SF | VA | RW |  |  | VAChaMax | Setpoint for maximum charging VA. | STO | DSTO | ChaVAMax | setMag.f | ASG | SP
124 | Storage | 7 |  | MinRsvPct |  |  | uint16 |  | MinRsvPct_SF | % WChaMax | RW |  |  | MinRsvPct | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage. | STO | DSTO | UseWhMinPct | setMag.f | ASG | SP |  |  |  |  | IEC 61850 also defines maximum reserve in percentage of max Capacity
124 | Storage | 8 |  | ChaState |  |  | uint16 |  | ChaState_SF | % AhrRtg |  |  |  | ChaState | Currently available energy as a percent of the capacity rating. | STO | DSTO | UseSocPct | mag.f | MV | MX |  |  |  |  | Another IEC 61850 DO SocEffWhPct takes degradation into account
124 | Storage | 9 |  | StorAval |  |  | uint16 |  | StorAval_SF | AH |  |  |  | StorAval | State of charge (ChaState) minus storage reserve (MinRsvPct) times capacity rating (AhrRtg). | STO | DSTO | AvlDschW | mag.f | MV | MX |  |  |  |  | This parameters refers to the available discharging power. It can also be calculated using other IEC 61850 parameters.
124 | Storage | 10 |  | InBatV |  |  | uint16 |  | InBatV_SF | V |  |  |  | InBatV | Internal battery voltage. | [9 empty] | x | currently not considered in our IEC 61850 data model, could be one DO in LN DBAT, we have excluded DBAT on purpose.
124 | Storage | 11 |  | ChaSt |  |  | enum16 | [6 empty] | ChaSt | Charge status of storage device. Enumerated value. | [8 empty] | x | x | This can be determined by combining other IEC 61850 parameters. IEC 61850 does not have such a DO to express the charging state explicitly.
124 | Storage |  |  | OFF | 1
124 | Storage |  |  | EMPTY | 2
124 | Storage |  |  | DISCHARGING | 3
124 | Storage |  |  | CHARGING | 4
124 | Storage |  |  | FULL | 5
124 | Storage |  |  | HOLDING | 6
124 | Storage |  |  | TESTING | 7
124 | Storage | 12 |  | OutWRte |  |  | int16 |  | InOutWRte_SF | % WDisChaMax | RW |  |  | OutWRte | Percent of max discharge rate. | STO | DSTO | OutWSet | setMag.f | ASG | SP |  |  | x |  | Charging rate is uderstood as charing power here, when it comes to the battery settings. This should be replaced by DSTO.WSpt.ctlVal, as soon as it is properly supported in libiec61850
124 | Storage | 13 |  | InWRte |  |  | int16 |  | InOutWRte_SF | % WChaMax | RW |  |  | InWRte | Percent of max charging rate. | STO | DSTO | OutWSet | setMag.f | ASG | SP |  |  | x |  | Charging rate is uderstood as charing power here, when it comes to the battery settings. This should be replaced by DSTO.WSpt.ctlVal, as soon as it is properly supported in libiec61850. Attention, in IEC 61850 we have only one SP, with two directions, besides the value is not in percentage, but in Watt.
124 | Storage | 14 |  | InOutWRte_WinTms |  |  | uint16 |  |  | Secs | RW |  |  | InOutWRte_WinTms | Time window for charge/discharge rate change. | [9 empty] | x | Time management parameters are not implemented in our IEC61850 data model.
124 | Storage | 15 |  | InOutWRte_RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | InOutWRte_RvrtTms | Timeout period for charge/discharge rate. | [9 empty] | x | Time management parameters are not implemented in our IEC61850 data model.
124 | Storage | 16 |  | InOutWRte_RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | InOutWRte_RmpTms | Ramp time for moving from current setpoint to new setpoint. | [9 empty] | x | Time management parameters are not implemented in our IEC61850 data model.
124 | Storage | 17 |  | ChaGriSet |  |  | enum16 |  |  |  | RW |  |  |  |  | STO | DSTO | ChaSrc | setVal.f | ENG | SP |  |  | x |  | IEC 61850 has defined the DO ChaSrc with 3 charging modes, which is definitely incompatible with SunSpec parameter ChaGriSet
124 | Storage |  |  | PV | 0
124 | Storage |  |  | GRID | 1
124 | Storage | 18 |  | WChaMax_SF |  |  | sunssf |  |  |  |  | M |  | WChaMax_SF | Scale factor for maximum charge. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib. Bur it could be used during the calculation to determine the exact value of the associated parameters.
124 | Storage | 19 |  | WChaDisChaGra_SF |  |  | sunssf |  |  |  |  | M |  | WChaDisChaGra_SF | Scale factor for maximum charge and discharge rate. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib. Bur it could be used during the calculation to determine the exact value of the associated parameters.
124 | Storage | 20 |  | VAChaMax_SF |  |  | sunssf | [6 empty] | VAChaMax_SF | Scale factor for maximum charging VA. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib. Bur it could be used during the calculation to determine the exact value of the associated parameters.
124 | Storage | 21 |  | MinRsvPct_SF |  |  | sunssf | [6 empty] | MinRsvPct_SF | Scale factor for minimum reserve percentage. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib. Bur it could be used during the calculation to determine the exact value of the associated parameters.
124 | Storage | 22 |  | ChaState_SF |  |  | sunssf | [6 empty] | ChaState_SF | Scale factor for available energy percent. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib. Bur it could be used during the calculation to determine the exact value of the associated parameters.
124 | Storage | 23 |  | StorAval_SF |  |  | sunssf | [6 empty] | StorAval_SF | Scale factor for state of charge. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib. Bur it could be used during the calculation to determine the exact value of the associated parameters.
124 | Storage | 24 |  | InBatV_SF |  |  | sunssf | [6 empty] | InBatV_SF | Scale factor for battery voltage. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib. Bur it could be used during the calculation to determine the exact value of the associated parameters.
124 | Storage | 25 |  | InOutWRte_SF |  |  | sunssf | [6 empty] | InOutWRte_SF | Scale factor for percent charge/discharge rate. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib. Bur it could be used during the calculation to determine the exact value of the associated parameters.
125 | Pricing | 0 |  | ID | 125 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier | [9 empty] | x | no matching required
125 | Pricing | 1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length | [9 empty] | x | no matching required
125 | Pricing | 2 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Is price-based charge/discharge mode active? | [9 empty] | x | currently not considered in our IEC 61850 data model
125 | Pricing |  |  | ENABLE | 0
125 | Pricing | 3 |  | SigType |  |  | enum16 |  |  |  | RW |  |  | SigType | Meaning of the pricing signal. When a Price schedule is used, type must match the schedule range variable description. | [9 empty] | x | currently not considered in our IEC 61850 data model
125 | Pricing |  |  | UNKNOWN | 0
125 | Pricing |  |  | ABSOLUTE | 1
125 | Pricing |  |  | RELATIVE | 2
125 | Pricing |  |  | MULTIPLIER | 3
125 | Pricing |  |  | LEVEL | 4
125 | Pricing | 4 |  | Sig |  |  | int16 |  | Sig_SF |  | RW | M |  | Sig | Utility/ESP specific pricing signal. Content depends on pricing signal type. When H/M/L type is specified. Low=0; Med=1; High=2. | [9 empty] | x | currently not considered in our IEC 61850 data model
125 | Pricing | 5 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for charge/discharge pricing change. | [9 empty] | x | Time management parameters are not implemented in our IEC61850 data model.
125 | Pricing | 6 |  | RvtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvtTms | Timeout period for charge/discharge pricing change. | [9 empty] | x | Time management parameters are not implemented in our IEC61850 data model.
125 | Pricing | 7 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current charge or discharge level to new level. | [9 empty] | x | Time management parameters are not implemented in our IEC61850 data model.
125 | Pricing | 8 |  | Sig_SF |  |  | sunssf |  |  |  |  | M |  | Sig_SF | Pricing signal scale factor. | [9 empty] | x | The scale factor could be very useful, yet not supported in the pySunSpec lib.
125 | Pricing | 9 |  | Pad |  |  | pad | [17 empty] | x | no matching required
213 | wye-connect three phase (abcn) meter | 0 |  | ID | 214 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier | [9 empty] | x | no matching required
213 | wye-connect three phase (abcn) meter | 1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length | [9 empty] | x | no matching required
213 | wye-connect three phase (abcn) meter | 2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | Total AC Current | PCC | MMXU | A | res.cVal.mag.f | WYE | MX |  |  |  |  | Special attention must be paid for the metering values. 201-204 and 211-214 (float) have similar parameter sheets. Only 213 is included in this mapping table. In addition, it must be clarified what is measured, only the PV or house PCC? For a simple demonstration, it is assumed that the meter values are delivered by meters located at house PCC.
213 | wye-connect three phase (abcn) meter | 4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current | PCC | MMXU | A | phsA.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 6 |  | AphB |  |  | float32 |  |  | A |  | M |  | Amps PhaseB | Phase B Current | PCC | MMXU | A | phsB.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 8 |  | AphC |  |  | float32 |  |  | A |  | M |  | Amps PhaseC | Phase C Current | PCC | MMXU | A | phsC.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 10 |  | PhV |  |  | float32 |  |  | V |  |  |  | Voltage LN | Line to Neutral AC Voltage (average of active phases) | PCC | MMXU | PhV | neut.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 12 |  | PhVphA |  |  | float32 |  |  | V |  |  |  | Phase Voltage AN | Phase Voltage AN | PCC | MMXU | PhV | phsA.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 14 |  | PhVphB |  |  | float32 |  |  | V |  |  |  | Phase Voltage BN | Phase Voltage BN | PCC | MMXU | PhV | phsB.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 16 |  | PhVphC |  |  | float32 |  |  | V |  |  |  | Phase Voltage CN | Phase Voltage CN | PCC | MMXU | PhV | phsC.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 18 |  | PPV |  |  | float32 |  |  | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases) | [9 empty] | x | not available in IEC 61850, can be calculated by taking the mean of active phases
213 | wye-connect three phase (abcn) meter | 20 |  | PPVphAB |  |  | float32 |  |  | V |  | M |  | Phase Voltage AB | Phase Voltage AB | PCC | MMXU | PPV | phsAB.cVal.mag.f | DEL | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 22 |  | PPVphBC |  |  | float32 |  |  | V |  | M |  | Phase Voltage BC | Phase Voltage BC | PCC | MMXU | PPV | phsBC.cVal.mag.f | DEL | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 24 |  | PPVphCA |  |  | float32 |  |  | V |  | M |  | Phase Voltage CA | Phase Voltage CA | PCC | MMXU | PPV | phsCA.cVal.mag.f | DEL | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 26 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Frequency | PCC | MMXU | Hz | mag.f | MV | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 28 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | Total Real Power | PCC | MMXU | TotW | mag.f | MV | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 30 |  | WphA |  |  | float32 |  |  | W |  |  |  | Watts phase A |  | PCC | MMXU | W | phsA.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 32 |  | WphB |  |  | float32 |  |  | W |  |  |  | Watts phase B |  | PCC | MMXU | W | phsB.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 34 |  | WphC |  |  | float32 |  |  | W |  |  |  | Watts phase C |  | PCC | MMXU | W | phsC.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 36 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power | PCC | MMXU | TotVA | mag.f | MV | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 38 |  | VAphA |  |  | float32 |  |  | VA |  |  |  | VA phase A |  | PCC | MMXU | VA | phsA.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 40 |  | VAphB |  |  | float32 |  |  | VA |  |  |  | VA phase B |  | PCC | MMXU | VA | phsB.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 42 |  | VAphC |  |  | float32 |  |  | VA |  |  |  | VA phase C |  | PCC | MMXU | VA | phsC.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 44 |  | VAR |  |  | float32 |  |  | var |  |  |  | VAR | Reactive Power | PCC | MMXU | TotVAr | mag.f | MV | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 46 |  | VARphA |  |  | float32 |  |  | var |  |  |  | VAR phase A |  | PCC | MMXU | Var | phsA.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 48 |  | VARphB |  |  | float32 |  |  | var |  |  |  | VAR phase B |  | PCC | MMXU | Var | phsB.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 50 |  | VARphC |  |  | float32 |  |  | var |  |  |  | VAR phase C |  | PCC | MMXU | Var | phsC.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 52 |  | PF |  |  | float32 |  |  | PF |  |  |  | PF | Power Factor | PCC | MMXU | TotPF | mag.f | MV | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 54 |  | PFphA |  |  | float32 |  |  | PF |  |  |  | PF phase A |  | PCC | MMXU | PF | phsA.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 56 |  | PFphB |  |  | float32 |  |  | PF |  |  |  | PF phase B |  | PCC | MMXU | PF | phsB.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 58 |  | PFphC |  |  | float32 |  |  | PF |  |  |  | PF phase C |  | PCC | MMXU | PF | phsC.cVal.mag.f | WYE | MX |  |  |  |  | Duplicates of PV.MMXU.XXX, parameters in 214 are not considered as part of the data interface, except for the case in which the meter values represents PCC measurement.
213 | wye-connect three phase (abcn) meter | 60 |  | TotWhExp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported | PCC | MMTR | SupWh | actVal | BCR | ST |  |  |  |  | the DO actVal represents an integer value!
213 | wye-connect three phase (abcn) meter | 62 |  | TotWhExpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase A | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 64 |  | TotWhExpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase B | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 66 |  | TotWhExpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase C | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 68 |  | TotWhImp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported | PCC | MMTR | DmdWh | actVal | BCR | ST |  |  |  |  | the DO actVal represents an integer value!
213 | wye-connect three phase (abcn) meter | 70 |  | TotWhImpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase A | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 72 |  | TotWhImpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase B | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 74 |  | TotWhImpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase C | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 76 |  | TotVAhExp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported | PCC | MMTR | TotVAh | actVal | BCR | ST |  |  |  |  | Total apparent VA-hours import/export is defined as net value in IEC 61850 MMTR -> take the difference between export and import to get Tot
213 | wye-connect three phase (abcn) meter | 78 |  | TotVAhExpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase A | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 80 |  | TotVAhExpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase B | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 82 |  | TotVAhExpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase C | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 84 |  | TotVAhImp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported | PCC | MMTR | TotVAh | actVal | BCR | ST |  | -1
213 | wye-connect three phase (abcn) meter | 86 |  | TotVAhImpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase A | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 88 |  | TotVAhImpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase B | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 90 |  | TotVAhImpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase C | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 92 |  | TotVArhImpQ1 |  |  | float32 |  |  | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1 | PCC | MMTR | SupVArh | actVal | BCR | ST |  |  |  |  | LN MMTR of IEC61850 only distinguishes between supply and demand, one needs to sum up two quadrants to get the total value.
213 | wye-connect three phase (abcn) meter | 94 |  | TotVArhImpQ1phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase A | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 96 |  | TotVArhImpQ1phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase B | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 98 |  | TotVArhImpQ1phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase C | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 100 |  | TotVArhImpQ2 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2 | PCC | MMTR | SupVArh | actVal | BCR | ST
213 | wye-connect three phase (abcn) meter | 102 |  | TotVArhImpQ2phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase A | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 104 |  | TotVArhImpQ2phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase B | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 106 |  | TotVArhImpQ2phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase C | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 108 |  | TotVArhExpQ3 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3 | PCC | MMTR | DmdVArh | actVal | BCR | ST
213 | wye-connect three phase (abcn) meter | 110 |  | TotVArhExpQ3phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase A | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 112 |  | TotVArhExpQ3phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase B | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 114 |  | TotVArhExpQ3phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase C | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 116 |  | TotVArhExpQ4 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4 | PCC | MMTR | DmdVArh | actVal | BCR | ST
213 | wye-connect three phase (abcn) meter | 118 |  | TotVArhExpQ4phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 120 |  | TotVArhExpQ4phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 122 |  | TotVArhExpQ4phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C | [10 empty] | x | This detail grade is not considered in IEC 61850.
213 | wye-connect three phase (abcn) meter | 124 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags | [9 empty] | x | events are not implemented in our IEC 61850 data model
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_Power_Failure | 2
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_Under_Voltage | 3
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_Low_PF | 4
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_Over_Current | 5
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_Over_Voltage | 6
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_Missing_Sensor | 7
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_Reserved1 | 8
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_Reserved2 | 9
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_Reserved3 | 10
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_Reserved4 | 11
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_Reserved5 | 12
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_Reserved6 | 13
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_Reserved7 | 14
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_Reserved8 | 15
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_OEM01 | 16
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_OEM02 | 17
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_OEM03 | 18
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_OEM04 | 19
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_OEM05 | 20
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_OEM06 | 21
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_OEM07 | 22
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_OEM08 | 23
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_OEM09 | 24
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_OEM10 | 25
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_OEM11 | 26
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_OEM12 | 27
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_OEM13 | 28
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_OEM14 | 29
213 | wye-connect three phase (abcn) meter |  |  | M_EVENT_OEM15 | 30
302 | Irradiance Model | 0 |  | ID | 302 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier | [9 empty] | x | no matching required
302 | Irradiance Model | 1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length | [9 empty] | x | no matching required
302 | Irradiance Model |  |  | irradiance.repeating |  | 0 | group | [17 empty] | x | not relevant
302 | Irradiance Model |  | 0 | GHI |  |  | uint16 |  |  | W/m2 |  |  |  | GHI | Global Horizontal Irradiance | METEO | MMET | HorInsol | mag.f | MV | MX
302 | Irradiance Model |  | 1 | POAI |  |  | uint16 |  |  | W/m2 |  |  |  | POAI | Plane-of-Array Irradiance | METEO | MMET | PoaInsol | mag.f | MV | MX
302 | Irradiance Model |  | 2 | DFI |  |  | uint16 |  |  | W/m2 |  |  |  | DFI | Diffuse Irradiance | METEO | MMET | DffInsol | mag.f | MV | MX
302 | Irradiance Model |  | 3 | DNI |  |  | uint16 |  |  | W/m2 |  |  |  | DNI | Direct Normal Irradiance | METEO | MMET | DctInsol | mag.f | MV | MX
302 | Irradiance Model |  | 4 | OTI |  |  | uint16 |  |  | W/m2 |  |  |  | OTI | Other Irradiance | [9 empty] | x | not specific enough, excluded
304 | Inclinometer Model | 0 |  | ID | 304 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier | [9 empty] | x | no matching required
304 | Inclinometer Model | 1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length | [9 empty] | x | no matching required
304 | Inclinometer Model |  |  | inclinometer.incl |  | 0 | group | [17 empty] | x | not relevant
304 | Inclinometer Model |  | 0 | Inclx |  |  | int32 |  | -2 | Degrees |  | M |  | X | X-Axis inclination | [9 empty] | x | panel inclination is not considered in our IEC 61850 data model
304 | Inclinometer Model |  | 2 | Incly |  |  | int32 |  | -2 | Degrees |  |  |  | Y | Y-Axis inclination | [9 empty] | x | panel inclination is not considered in our IEC 61850 data model
304 | Inclinometer Model |  | 4 | Inclz |  |  | int32 |  | -2 | Degrees |  |  |  | Z | Z-Axis inclination | [9 empty] | x | panel inclination is not considered in our IEC 61850 data model
305 | GPS | 2 |  | Tm |  |  | string | 6 |  | hhmmss.sssZ |  |  |  | Tm | UTC 24 hour time stamp to millisecond hhmmss.sssZ format | [9 empty] | x | Currently we have not implemented any methods to validate DER system time. Always assume the PV system delivers data with correct local/UTC time.
305 | GPS | 8 |  | Date |  |  | string | 4 |  | YYYYMMDD |  |  |  | Date | UTC Date string YYYYMMDD format | [9 empty] | x | Currently we have not implemented any methods to validate DER system time. Always assume the PV system delivers data with correct local/UTC time.
305 | GPS | 12 |  | Loc |  |  | string | 20 |  | text |  |  |  | Location | Location string (40 chars max) | CLS | LPHD | PhyNam | longitude | [6 empty] | Assume that GPS data is asscoiated with the CLS
305 | GPS | 32 |  | Lat |  |  | int32 |  | -7 | Degrees |  |  |  | Lat | Latitude with seven degrees of precision | CLS | LPHD | PhyNam | latitude | [6 empty] | Assume that GPS data is asscoiated with the CLS
305 | GPS | 34 |  | Long |  |  | int32 |  | -7 | Degrees |  |  |  | Long | Longitude with seven degrees of precision | CLS | LPHD | PhyNam | longitude | [6 empty] | Assume that GPS data is asscoiated with the CLS
305 | GPS | 36 |  | Alt |  |  | int32 |  |  | meters |  |  |  | Altitude | Altitude measurement in meters | CLS | LPHD | PhyNam | altitude | [6 empty] | Assume that GPS data is asscoiated with the CLS
306 | Reference Point Model | 2 |  | GHI |  |  | uint16 |  |  | W/m2 |  |  |  | GHI | Global Horizontal Irradiance | [9 empty] | x | reference point is not considered in our IEC 61850 data model. If the PV itself can not deliver METEO data, then the data from the nearest weather station will be used as reference.
306 | Reference Point Model | 3 |  | A |  |  | uint16 |  |  | W/m2 |  |  |  | Amps | Current measurement at reference point | [9 empty] | x | reference point is not considered in our IEC 61850 data model. If the PV itself can not deliver METEO data, then the data from the nearest weather station will be used as reference.
306 | Reference Point Model | 4 |  | V |  |  | uint16 |  |  | W/m2 |  |  |  | Voltage | Voltage measurement at reference point | [9 empty] | x | reference point is not considered in our IEC 61850 data model. If the PV itself can not deliver METEO data, then the data from the nearest weather station will be used as reference.
306 | Reference Point Model | 5 |  | Tmp |  |  | uint16 |  |  | W/m2 |  |  |  | Temperature | Temperature measurement at reference point | [9 empty] | x | reference point is not considered in our IEC 61850 data model. If the PV itself can not deliver METEO data, then the data from the nearest weather station will be used as reference.
307 | Base Met | 2 |  | TmpAmb |  |  | int16 |  | -1 | C |  |  |  | Ambient Temperature |  | METEO | MMET | EnvTmp | mag.f | MV | MX
307 | Base Met | 3 |  | RH |  |  | int16 |  |  | Pct |  |  |  | Relative Humidity |  | METEO | MMET | EnvHum | mag.f | MV | MX
307 | Base Met | 4 |  | Pres |  |  | int16 |  |  | HPa |  |  |  | Barometric Pressure |  | METEO | MMET | EnvPres | mag.f | MV | MX
307 | Base Met | 5 |  | WndSpd |  |  | int16 |  |  | mps |  |  |  | Wind Speed |  | METEO | MMET | VerWdSpd | mag.f | MV | MX
307 | Base Met | 6 |  | WndDir |  |  | int16 |  |  | deg |  |  |  | Wind Direction |  | METEO | MMET | VerWdDir | mag.f | MV | MX
307 | Base Met | 7 |  | Rain |  |  | int16 |  |  | mm |  |  |  | Rainfall |  | METEO | MMET | RnFll | mag.f | MV | MX
307 | Base Met | 8 |  | Snw |  |  | int16 |  |  | mm |  |  |  | Snow Depth |  | METEO | MMET | SnwCvr | mag.f | MV | MX
307 | Base Met | 9 |  | PPT |  |  | int16 | [6 empty] | Precipitation Type | Precipitation Type (WMO 4680 SYNOP code reference) | [9 empty] | x | not considered in our IEC 61850 data model
307 | Base Met | 10 |  | ElecFld |  |  | int16 |  |  | Vm |  |  |  | Electric Field | [10 empty] | x | not available in IEC 61850
307 | Base Met | 11 |  | SurWet |  |  | int16 |  |  | kO |  |  |  | Surface Wetness | [10 empty] | x | not available in IEC 61850
307 | Base Met | 12 |  | SoilWet |  |  | int16 |  |  | Pct |  |  |  | Soil Wetness | [10 empty] | x | not available in IEC 61850

## SunSpec_700_Series
Model ID | Model Label | Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | IEC 61850 DA | FC | Source
701 | DER AC Measurement | Wiring Type
701 | DER AC Measurement | 2 |  | ACType |  |  | enum16 |  |  |  |  | M |  | AC Wiring Type | AC wiring type.
701 | DER AC Measurement |  |  | SINGLE_PHASE | 0 | [8 empty] | Single Phase
701 | DER AC Measurement |  |  | SPLIT_PHASE | 1 | [8 empty] | Split Phase
701 | DER AC Measurement |  |  | THREE_PHASE | 2 | [8 empty] | Three Phase
701 | DER AC Measurement | Operating State
701 | DER AC Measurement | 3 |  | St |  |  | enum16 | [6 empty] | Operating State | Operating state of the DER.
701 | DER AC Measurement |  |  | OFF | 0 | [8 empty] | Off
701 | DER AC Measurement |  |  | ON | 1 | [8 empty] | On
701 | DER AC Measurement | Inverter State
701 | DER AC Measurement | 4 |  | InvSt |  |  | enum16 | [6 empty] | Inverter State | Enumerated value. Inverter state.
701 | DER AC Measurement |  |  | OFF | 0
701 | DER AC Measurement |  |  | SLEEPING | 1
701 | DER AC Measurement |  |  | STARTING | 2
701 | DER AC Measurement |  |  | RUNNING | 3
701 | DER AC Measurement |  |  | THROTTLED | 4
701 | DER AC Measurement |  |  | SHUTTING_DOWN | 5
701 | DER AC Measurement |  |  | FAULT | 6
701 | DER AC Measurement |  |  | STANDBY | 7
701 | DER AC Measurement | Grid Connection State
701 | DER AC Measurement | 5 |  | ConnSt |  |  | enum16 | [6 empty] | Grid Connection State | Grid connection state of the DER.
701 | DER AC Measurement |  |  | DISCONNECTED | 0 | [8 empty] | Disconnected | Disconnected from the grid.
701 | DER AC Measurement |  |  | CONNECTED | 1 | [8 empty] | Connected | Connected to the grid.
701 | DER AC Measurement | Alarms
701 | DER AC Measurement | 6 |  | Alrm |  |  | bitfield32 | [6 empty] | Alarm Bitfield | Active alarms for the DER.
701 | DER AC Measurement |  |  | GROUND_FAULT | 0 | [8 empty] | Ground Fault
701 | DER AC Measurement |  |  | DC_OVER_VOLT | 1 | [8 empty] | DC Over Voltage
701 | DER AC Measurement |  |  | AC_DISCONNECT | 2 | [8 empty] | AC Disconnect Open
701 | DER AC Measurement |  |  | DC_DISCONNECT | 3 | [8 empty] | DC Disconnect Open
701 | DER AC Measurement |  |  | GRID_DISCONNECT | 4 | [8 empty] | Grid Disconnect
701 | DER AC Measurement |  |  | CABINET_OPEN | 5 | [8 empty] | Cabinet Open
701 | DER AC Measurement |  |  | MANUAL_SHUTDOWN | 6 | [8 empty] | Manual Shutdown
701 | DER AC Measurement |  |  | OVER_TEMP | 7 | [8 empty] | Over Temperature
701 | DER AC Measurement |  |  | OVER_FREQUENCY | 8 | [8 empty] | Frequency Above Limit
701 | DER AC Measurement |  |  | UNDER_FREQUENCY | 9 | [8 empty] | Frequency Under Limit
701 | DER AC Measurement |  |  | AC_OVER_VOLT | 10 | [8 empty] | AC Voltage Above Limit
701 | DER AC Measurement |  |  | AC_UNDER_VOLT | 11 | [8 empty] | AC Voltage Under Limit
701 | DER AC Measurement |  |  | BLOWN_STRING_FUSE | 12 | [8 empty] | Blown String Fuse On Input
701 | DER AC Measurement |  |  | UNDER_TEMP | 13 | [8 empty] | Under Temperature
701 | DER AC Measurement |  |  | MEMORY_LOSS | 14 | [8 empty] | Generic Memory Or Communication Error (Internal)
701 | DER AC Measurement |  |  | HW_TEST_FAILURE | 15 | [8 empty] | Hardware Test Failure
701 | DER AC Measurement |  |  | MANUFACTURER_ALRM | 16 | [8 empty] | Manufacturer Alarm | Manufacturer alarm, see ManAlrmInfo field for more information.
701 | DER AC Measurement | 8 |  | DERMode |  |  | bitfield32 | [6 empty] | DER Operational Characteristics | Current operational characteristics of the DER.
701 | DER AC Measurement |  |  | GRID_FOLLOWING | 0 | [8 empty] | Grid Following | The DER is operating as part of a larger grid.
701 | DER AC Measurement |  |  | GRID_FORMING | 1 | [8 empty] | Grid Forming | The DER is providing the grid.
701 | DER AC Measurement |  |  | PV_CLIPPED | 2 | [8 empty] | PV Output Clipped | The PV output is clipped.
701 | DER AC Measurement | Summary
701 | DER AC Measurement | 10 |  | W |  |  | int16 |  | W_SF | W |  |  |  | Active Power | Total active power. Active power is positive for DER generation and negative for absorption.
701 | DER AC Measurement | 11 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | Apparent Power | Total apparent power.
701 | DER AC Measurement | 12 |  | Var |  |  | int16 |  | Var_SF | Var |  |  |  | Reactive Power | Total reactive power.
701 | DER AC Measurement | 13 |  | PF |  |  | int16 |  | PF_SF |  |  |  |  | Power Factor | Power factor. The sign of power factor should be the sign of active power.
701 | DER AC Measurement | 14 |  | A |  |  | int16 |  | A_SF | A |  |  |  | Total AC Current | Total AC current.
701 | DER AC Measurement | 15 |  | LLV |  |  | uint16 |  | V_SF | V |  |  |  | Voltage LL | Line to line AC voltage as an average of active phases.
701 | DER AC Measurement | 16 |  | LNV |  |  | uint16 |  | V_SF | V |  |  |  | Voltage LN | Line to neutral AC voltage as an average of active phases.
701 | DER AC Measurement | 17 |  | Hz |  |  | uint32 |  | Hz_SF | Hz |  |  |  | Frequency | AC frequency.
701 | DER AC Measurement | 19 |  | TotWhInj |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Energy Injected | Total active energy injected (Quadrants 1 & 4).
701 | DER AC Measurement | 23 |  | TotWhAbs |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Energy Absorbed | Total active energy absorbed (Quadrants 2 & 3).
701 | DER AC Measurement | 27 |  | TotVarhInj |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Reactive Energy Inj | Total reactive energy injected (Quadrants 1 & 2).
701 | DER AC Measurement | 31 |  | TotVarhAbs |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Reactive Energy Abs | Total reactive energy absorbed (Quadrants 3 & 4).
701 | DER AC Measurement | Temperatures
701 | DER AC Measurement | 35 |  | TmpAmb |  |  | int16 |  | Tmp_SF | C |  |  |  | Ambient Temperature | Ambient temperature.
701 | DER AC Measurement | 36 |  | TmpCab |  |  | int16 |  | Tmp_SF | C |  |  |  | Cabinet Temperature | Cabinet temperature.
701 | DER AC Measurement | 37 |  | TmpSnk |  |  | int16 |  | Tmp_SF | C |  |  |  | Heat Sink Temperature | Heat sink temperature.
701 | DER AC Measurement | 38 |  | TmpTrns |  |  | int16 |  | Tmp_SF | C |  |  |  | Transformer Temperature | Transformer temperature.
701 | DER AC Measurement | 39 |  | TmpSw |  |  | int16 |  | Tmp_SF | C |  |  |  | IGBT/MOSFET Temperature | IGBT/MOSFET temperature.
701 | DER AC Measurement | 40 |  | TmpOt |  |  | int16 |  | Tmp_SF | C |  |  |  | Other Temperature | Other temperature.
701 | DER AC Measurement | L1
701 | DER AC Measurement | 41 |  | WL1 |  |  | int16 |  | W_SF | W |  |  |  | Watts L1 | Active power L1.
701 | DER AC Measurement | 42 |  | VAL1 |  |  | int16 |  | VA_SF | VA |  |  |  | VA L1 | Apparent power L1.
701 | DER AC Measurement | 43 |  | VarL1 |  |  | int16 |  | Var_SF | Var |  |  |  | Var L1 | Reactive power L1.
701 | DER AC Measurement | 44 |  | PFL1 |  |  | int16 |  | PF_SF |  |  |  |  | PF L1 | Power factor phase L1.
701 | DER AC Measurement | 45 |  | AL1 |  |  | int16 |  | A_SF | A |  |  |  | Amps L1 | Current phase L1.
701 | DER AC Measurement | 46 |  | VL1L2 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L1-L2 | Phase voltage L1-L2.
701 | DER AC Measurement | 47 |  | VL1 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L1-N | Phase voltage L1-N.
701 | DER AC Measurement | 48 |  | TotWhInjL1 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Inj L1 | Total active energy injected L1.
701 | DER AC Measurement | 52 |  | TotWhAbsL1 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Abs L1 | Total active energy absorbed L1.
701 | DER AC Measurement | 56 |  | TotVarhInjL1 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Inj L1 | Total reactive energy injected L1.
701 | DER AC Measurement | 60 |  | TotVarhAbsL1 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Abs L1 | Total reactive energy absorbed L1.
701 | DER AC Measurement | L2
701 | DER AC Measurement | 64 |  | WL2 |  |  | int16 |  | W_SF | W |  |  |  | Watts L2 | Active power L2.
701 | DER AC Measurement | 65 |  | VAL2 |  |  | int16 |  | VA_SF | VA |  |  |  | VA L2 | Apparent power L2.
701 | DER AC Measurement | 66 |  | VarL2 |  |  | int16 |  | Var_SF | Var |  |  |  | Var L2 | Reactive power L2.
701 | DER AC Measurement | 67 |  | PFL2 |  |  | int16 |  | PF_SF |  |  |  |  | PF L2 | Power factor L2.
701 | DER AC Measurement | 68 |  | AL2 |  |  | int16 |  | A_SF | A |  |  |  | Amps L2 | Current L2.
701 | DER AC Measurement | 69 |  | VL2L3 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L2-L3 | Phase voltage L2-L3.
701 | DER AC Measurement | 70 |  | VL2 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L2-N | Phase voltage L2-N.
701 | DER AC Measurement | 71 |  | TotWhInjL2 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Inj L2 | Total active energy injected L2.
701 | DER AC Measurement | 75 |  | TotWhAbsL2 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Abs L2 | Total active energy absorbed L2.
701 | DER AC Measurement | 79 |  | TotVarhInjL2 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Inj L2 | Total reactive energy injected L2.
701 | DER AC Measurement | 83 |  | TotVarhAbsL2 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Abs L2 | Total reactive energy absorbed L2.
701 | DER AC Measurement | L3
701 | DER AC Measurement | 87 |  | WL3 |  |  | int16 |  | W_SF | W |  |  |  | Watts L3 | Active power L3.
701 | DER AC Measurement | 88 |  | VAL3 |  |  | int16 |  | VA_SF | VA |  |  |  | VA L3 | Apparent power L3.
701 | DER AC Measurement | 89 |  | VarL3 |  |  | int16 |  | Var_SF | Var |  |  |  | Var L3 | Reactive power L3.
701 | DER AC Measurement | 90 |  | PFL3 |  |  | int16 |  | PF_SF |  |  |  |  | PF L3 | Power factor L3.
701 | DER AC Measurement | 91 |  | AL3 |  |  | int16 |  | A_SF | A |  |  |  | Amps L3 | Current L3.
701 | DER AC Measurement | 92 |  | VL3L1 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L3-L1 | Phase voltage L3-L1.
701 | DER AC Measurement | 93 |  | VL3 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L3-N | Phase voltage L3-N.
701 | DER AC Measurement | 94 |  | TotWhInjL3 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Inj L3 | Total active energy injected L3.
701 | DER AC Measurement | 98 |  | TotWhAbsL3 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Abs L3 | Total active energy absorbed L3.
701 | DER AC Measurement | 102 |  | TotVarhInjL3 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Inj L3 | Total reactive energy injected L3.
701 | DER AC Measurement | 106 |  | TotVarhAbsL3 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Abs L3 | Total reactive energy absorbed L3.
701 | DER AC Measurement | Active Power Throttling
701 | DER AC Measurement | 110 |  | ThrotPct |  |  | uint16 |  |  | Pct |  |  |  | Throttling In Pct | Throttling in pct of maximum active power.
701 | DER AC Measurement | 111 |  | ThrotSrc |  |  | bitfield32 | [6 empty] | Throttle Source Information | Active throttling source.
701 | DER AC Measurement |  |  | MAX_W | 0
701 | DER AC Measurement |  |  | FIXED_W | 1
701 | DER AC Measurement |  |  | FIXED_VAR | 2
701 | DER AC Measurement |  |  | FIXED_PF | 3
701 | DER AC Measurement |  |  | VOLT_VAR | 4
701 | DER AC Measurement |  |  | FREQ_WATT | 5
701 | DER AC Measurement |  |  | DYN_REACT_CURR | 6
701 | DER AC Measurement |  |  | LVRT | 7
701 | DER AC Measurement |  |  | HVRT | 8
701 | DER AC Measurement |  |  | WATT_VAR | 9
701 | DER AC Measurement |  |  | VOLT_WATT | 10
701 | DER AC Measurement |  |  | SCHEDULED | 11
701 | DER AC Measurement |  |  | LFRT | 12
701 | DER AC Measurement |  |  | HFRT | 13
701 | DER AC Measurement |  |  | DERATED | 14
701 | DER AC Measurement | Scale Factors
701 | DER AC Measurement | 113 |  | A_SF |  |  | sunssf | [5 empty] | S | Current Scale Factor | Current scale factor.
701 | DER AC Measurement | 114 |  | V_SF |  |  | sunssf | [5 empty] | S | Voltage Scale Factor | Voltage scale factor.
701 | DER AC Measurement | 115 |  | Hz_SF |  |  | sunssf | [5 empty] | S | Frequency Scale Factor | Frequency scale factor.
701 | DER AC Measurement | 116 |  | W_SF |  |  | sunssf | [5 empty] | S | Active Power Scale Factor | Active power scale factor.
701 | DER AC Measurement | 117 |  | PF_SF |  |  | sunssf | [5 empty] | S | Power Factor Scale Factor | Power factor scale factor.
701 | DER AC Measurement | 118 |  | VA_SF |  |  | sunssf | [5 empty] | S | Apparent Power Scale Factor | Apparent power scale factor.
701 | DER AC Measurement | 119 |  | Var_SF |  |  | sunssf | [5 empty] | S | Reactive Power Scale Factor | Reactive power scale factor.
701 | DER AC Measurement | 120 |  | TotWh_SF |  |  | sunssf | [5 empty] | S | Active Energy Scale Factor | Active energy scale factor.
701 | DER AC Measurement | 121 |  | TotVarh_SF |  |  | sunssf | [5 empty] | S | Reactive Energy Scale Factor | Reactive energy scale factor.
701 | DER AC Measurement | 122 |  | Tmp_SF |  |  | sunssf | [5 empty] | S | Temperature Scale Factor | Temperature scale factor.
701 | DER AC Measurement | Manufacturer Alarm Information
701 | DER AC Measurement | 123 |  | MnAlrmInfo |  |  | string | 32 | [5 empty] | Manufacturer Alarm Info | Manufacturer alarm information. Valid if MANUFACTURER_ALRM indication is active.
702 | DER Capacity | Nameplate Ratings - Specifies capacity ratings
702 | DER Capacity | 2 |  | WMaxRtg |  |  | uint16 |  | W_SF | W |  |  | S | Active Power Max Rating | Maximum active power rating at unity power factor in watts.
702 | DER Capacity | 3 |  | WOvrExtRtg |  |  | uint16 |  | W_SF | W |  |  | S | Active Power (Over-Excited) Rating | Active power rating at specified over-excited power factor in watts.
702 | DER Capacity | 4 |  | WOvrExtRtgPF |  |  | uint16 |  | PF_SF |  |  |  | S | Specified Over-Excited PF | Specified over-excited power factor.
702 | DER Capacity | 5 |  | WUndExtRtg |  |  | uint16 |  | W_SF | W |  |  | S | Active Power (Under-Excited) Rating | Active power rating at specified under-excited power factor in watts.
702 | DER Capacity | 6 |  | WUndExtRtgPF |  |  | uint16 |  | PF_SF |  |  |  | S | Specified Under-Excited PF | Specified under-excited power factor.
702 | DER Capacity | 7 |  | VAMaxRtg |  |  | uint16 |  | VA_SF | VA |  |  | S | Apparent Power Max Rating | Maximum apparent power rating in voltamperes.
702 | DER Capacity | 8 |  | VarMaxInjRtg |  |  | uint16 |  | Var_SF | Var |  |  | S | Reactive Power Injected Rating | Maximum injected reactive power rating in vars.
702 | DER Capacity | 9 |  | VarMaxAbsRtg |  |  | uint16 |  | Var_SF | Var |  |  | S | Reactive Power Absorbed Rating | Maximum absorbed reactive power rating in vars.
702 | DER Capacity | 10 |  | WChaRteMaxRtg |  |  | uint16 |  | W_SF | W |  |  | S | Charge Rate Max Rating | Maximum active power charge rate in watts.
702 | DER Capacity | 11 |  | WDisChaRteMaxRtg |  |  | uint16 |  | W_SF | W |  |  | S | Discharge Rate Max Rating | Maximum active power discharge rate in watts.
702 | DER Capacity | 12 |  | VAChaRteMaxRtg |  |  | uint16 |  | VA_SF | VA |  |  | S | Charge Rate Max VA Rating | Maximum apparent power charge rate in voltamperes.
702 | DER Capacity | 13 |  | VADisChaRteMaxRtg |  |  | uint16 |  | VA_SF | VA |  |  | S | Discharge Rate Max VA Rating | Maximum apparent power discharge rate in voltamperes.
702 | DER Capacity | 14 |  | VNomRtg |  |  | uint16 |  | V_SF | V |  |  | S | AC Voltage Nominal Rating | AC voltage nominal rating.
702 | DER Capacity | 15 |  | VMaxRtg |  |  | uint16 |  | V_SF | V |  |  | S | AC Voltage Max Rating | AC voltage maximum rating.
702 | DER Capacity | 16 |  | VMinRtg |  |  | uint16 |  | V_SF | V |  |  | S | AC Voltage Min Rating | AC voltage minimum rating.
702 | DER Capacity | 17 |  | AMaxRtg |  |  | uint16 |  | A_SF | A |  |  | S | AC Current Max Rating | AC current maximum rating in amps.
702 | DER Capacity | 18 |  | PFOvrExtRtg |  |  | uint16 |  | PF_SF |  |  |  | S | PF Over-Excited Rating | Power factor over-excited rating.
702 | DER Capacity | 19 |  | PFUndExtRtg |  |  | uint16 |  | PF_SF |  |  |  | S | PF Under-Excited Rating | Power factor under-excited rating.
702 | DER Capacity | 20 |  | ReactSusceptRtg |  |  | uint16 |  | S_SF | S |  |  | S | Reactive Susceptance | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state.
702 | DER Capacity | 21 |  | NorOpCatRtg |  |  | enum16 | [5 empty] | S | Normal Operating Category | Normal operating performance category as specified in IEEE 1547-2018.
702 | DER Capacity |  |  | CAT_A | 0 | [8 empty] | Category A
702 | DER Capacity |  |  | CAT_B | 1 | [8 empty] | Category B
702 | DER Capacity | 22 |  | AbnOpCatRtg |  |  | enum16 | [5 empty] | S | Abnormal Operating Category | Abnormal operating performance category as specified in IEEE 1547-2018.
702 | DER Capacity |  |  | CAT_1 | 0 | [8 empty] | Category I
702 | DER Capacity |  |  | CAT_2 | 1 | [8 empty] | Category II
702 | DER Capacity |  |  | CAT_3 | 2 | [8 empty] | Category III
702 | DER Capacity | 23 |  | CtrlModes |  |  | bitfield32 | [5 empty] | S | Supported Control Modes | Supported control mode functions.
702 | DER Capacity |  |  | MAX_W | 0 | [8 empty] | Limit Maximum Active Power
702 | DER Capacity |  |  | FIXED_W | 1 | [8 empty] | Fixed Active Power
702 | DER Capacity |  |  | FIXED_VAR | 2 | [8 empty] | Fixed Reactive Power
702 | DER Capacity |  |  | FIXED_PF | 3 | [8 empty] | Fixed Power Factor
702 | DER Capacity |  |  | VOLT_VAR | 4 | [8 empty] | Volt-Var Function
702 | DER Capacity |  |  | FREQ_WATT | 5 | [8 empty] | Freq-Watt Function
702 | DER Capacity |  |  | DYN_REACT_CURR | 6 | [8 empty] | Dynamic Reactive Current Function
702 | DER Capacity |  |  | LV_TRIP | 7 | [8 empty] | Low-Voltage Trip
702 | DER Capacity |  |  | HV_TRIP | 8 | [8 empty] | High-Voltage Trip
702 | DER Capacity |  |  | WATT_VAR | 9 | [8 empty] | Watt-Var Function
702 | DER Capacity |  |  | VOLT_WATT | 10 | [8 empty] | Volt-Watt Function
702 | DER Capacity |  |  | SCHEDULED | 11 | [8 empty] | Scheduling
702 | DER Capacity |  |  | LF_TRIP | 12 | [8 empty] | Low-Frequency Trip
702 | DER Capacity |  |  | HF_TRIP | 13 | [8 empty] | High-Frequency Trip
702 | DER Capacity | 25 |  | IntIslandCatRtg |  |  | bitfield16 | [5 empty] | S | Intentional Island Categories | Intentional island categories.
702 | DER Capacity |  |  | UNCATEGORIZED | 0 | [8 empty] | Uncategorized
702 | DER Capacity |  |  | INT_ISL_CAPABLE | 1 | [8 empty] | Intentional Island-Capable
702 | DER Capacity |  |  | BLACK_START_CAPABLE | 2 | [8 empty] | Black Start-Capable
702 | DER Capacity |  |  | ISOCH_CAPABLE | 3 | [8 empty] | Isochronous-Capable
702 | DER Capacity | Settings - Used to adjust nameplate ratings
702 | DER Capacity | 26 |  | WMax |  |  | uint16 |  | W_SF | W | RW |  |  | Active Power Max Setting | Maximum active power setting used to adjust maximum active power setting.
702 | DER Capacity | 27 |  | WMaxOvrExt |  |  | uint16 |  | W_SF | W | RW |  |  | Active Power (Over-Excited) Setting | Active power setting at specified over-excited power factor in watts.
702 | DER Capacity | 28 |  | WOvrExtPF |  |  | uint16 |  | PF_SF |  | RW |  |  | Specified Over-Excited PF | Specified over-excited power factor.
702 | DER Capacity | 29 |  | WMaxUndExt |  |  | uint16 |  | W_SF | W | RW |  |  | Active Power (Under-Excited) Setting | Active power setting at specified under-excited power factor in watts.
702 | DER Capacity | 30 |  | WUndExtPF |  |  | uint16 |  | PF_SF |  | RW |  |  | Specified Under-Excited PF | Specified under-excited power factor.
702 | DER Capacity | 31 |  | VAMax |  |  | uint16 |  | VA_SF | VA | RW |  |  | Apparent Power Max Setting | Maximum apparent power setting used to adjust maximum apparent power rating.
702 | DER Capacity | 32 |  | VarMaxInj |  |  | uint16 |  | Var_SF | Var | RW |  |  | Reactive Power Injected Setting | Maximum injected reactive power setting used to adjust maximum injected reactive power rating.
702 | DER Capacity | 33 |  | VarMaxAbs |  |  | uint16 |  | Var_SF | Var | RW |  |  | Reactive Power Absorbed Setting | Maximum absorbed reactive power setting used to adjust maximum absorbed reactive power rating.
702 | DER Capacity | 34 |  | WChaRteMax |  |  | uint16 |  | W_SF | W | RW |  |  | Charge Rate Max Setting | Maximum active power charge rate setting used to adjust maximum active power charge rate rating.
702 | DER Capacity | 35 |  | WDisChaRteMax |  |  | uint16 |  | W_SF | W | RW |  |  | Discharge Rate Max Setting | Maximum active power discharge rate setting used to adjust maximum active power discharge rate rating.
702 | DER Capacity | 36 |  | VAChaRteMax |  |  | uint16 |  | VA_SF | VA | RW |  |  | Charge Rate Max VA Setting | Maximum apparent power charge rate setting used to adjust maximum apparent power charge rate rating.
702 | DER Capacity | 37 |  | VADisChaRteMax |  |  | uint16 |  | VA_SF | VA | RW |  |  | Discharge Rate Max VA Setting | Maximum apparent power discharge rate setting used to adjust maximum apparent power discharge rate rating.
702 | DER Capacity | 38 |  | VNom |  |  | uint16 |  | V_SF | V | RW |  |  | Nominal AC Voltage Setting | Nominal AC voltage setting.
702 | DER Capacity | 39 |  | VMax |  |  | uint16 |  | V_SF | V | RW |  |  | AC Voltage Max Setting | AC voltage maximum setting used to adjust AC voltage maximum rating.
702 | DER Capacity | 40 |  | VMin |  |  | uint16 |  | V_SF | V | RW |  |  | AC Voltage Min Setting | AC voltage minimum setting used to adjust AC voltage minimum rating.
702 | DER Capacity | 41 |  | AMax |  |  | uint16 |  | A_SF | A | RW |  |  | AC Current Max Setting | Maximum AC current setting used to adjust maximum AC current rating.
702 | DER Capacity | 42 |  | PFOvrExt |  |  | uint16 |  | PF_SF |  | RW |  |  | PF Over-Excited Setting | Power factor over-excited setting.
702 | DER Capacity | 43 |  | PFUndExt |  |  | uint16 |  | PF_SF |  | RW |  |  | PF Under-Excited Setting | Power factor under-excited setting.
702 | DER Capacity | 44 |  | IntIslandCat |  |  | bitfield16 |  |  |  | RW |  |  | Intentional Island Categories | Intentional island categories.
702 | DER Capacity |  |  | UNCATEGORIZED | 0 | [8 empty] | Uncategorized
702 | DER Capacity |  |  | INT_ISL_CAPABLE | 1 | [8 empty] | Intentional Island-Capable
702 | DER Capacity |  |  | BLACK_START_CAPABLE | 2 | [8 empty] | Black Start-Capable
702 | DER Capacity |  |  | ISOCH_CAPABLE | 3 | [8 empty] | Isochronous-Capable
702 | DER Capacity | Scale Factors
702 | DER Capacity | 45 |  | W_SF |  |  | sunssf | [5 empty] | S | Active Power Scale Factor | Active power scale factor.
702 | DER Capacity | 46 |  | PF_SF |  |  | sunssf | [5 empty] | S | Power Factor Scale Factor | Power factor scale factor.
702 | DER Capacity | 47 |  | VA_SF |  |  | sunssf | [5 empty] | S | Apparent Power Scale Factor | Apparent power scale factor.
702 | DER Capacity | 48 |  | Var_SF |  |  | sunssf | [5 empty] | S | Reactive Power Scale Factor | Reactive power scale factor.
702 | DER Capacity | 49 |  | V_SF |  |  | sunssf | [5 empty] | S | Voltage Scale Factor | Voltage scale factor.
702 | DER Capacity | 50 |  | A_SF |  |  | sunssf | [5 empty] | S | Current Scale Factor | Current scale factor.
702 | DER Capacity | 51 |  | S_SF |  |  | sunssf | [5 empty] | S | Susceptance Scale Factor | Susceptance scale factor.
703 | Enter Service | 2 |  | ES |  |  | enum16 |  |  |  | RW |  |  | Permit Enter Service | Permit enter service.
703 | Enter Service |  |  | DISABLED | 0
703 | Enter Service |  |  | ENABLED | 1
703 | Enter Service | 3 |  | ESVHi |  |  | uint16 |  | V_SF | Pct | RW |  |  | Enter Service Voltage High | Enter service voltage high threshold as percent of normal voltage.
703 | Enter Service | 4 |  | ESVLo |  |  | uint16 |  | V_SF | Pct | RW |  |  | Enter Service Voltage Low | Enter service voltage low threshold as percent of normal voltage.
703 | Enter Service | 5 |  | ESHzHi |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Enter Service Frequency High | Enter service frequency high threshold.
703 | Enter Service | 7 |  | ESHzLo |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Enter Service Frequency Low | Enter service frequency low threshold.
703 | Enter Service | 9 |  | ESDlyTms |  |  | uint32 |  |  | Secs | RW |  |  | Enter Service Delay Time | Enter service delay time in seconds.
703 | Enter Service | 11 |  | ESRndTms |  |  | uint32 |  |  | Secs | RW |  |  | Enter Service Random Delay | Enter service random delay in seconds.
703 | Enter Service | 13 |  | ESRmpTms |  |  | uint32 |  |  | Secs | RW |  |  | Enter Service Ramp Time | Enter service ramp time in seconds.
703 | Enter Service | 15 |  | ESDlyRemTms |  |  | uint32 |  |  | Secs |  |  |  | Enter Service Delay Remaining | Enter service delay time remaining in seconds.
703 | Enter Service | 17 |  | V_SF |  |  | sunssf | [5 empty] | S | Voltage Scale Factor | Voltage percentage scale factor.
703 | Enter Service | 18 |  | Hz_SF |  |  | sunssf | [5 empty] | S | Frequency Scale Factor | Frequency scale factor.
704 | DER AC controls model. | Set Power Factor (when injecting active power)
704 | DER AC controls model. | 2 |  | PFWInjEna |  |  | enum16 |  |  |  | RW |  |  | Power Factor Enable (W Inj) Enable | Power factor enable when injecting active power.
704 | DER AC controls model. |  |  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
704 | DER AC controls model. |  |  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
704 | DER AC controls model. | 3 |  | PFWInjEnaRvrt |  |  | enum16 |  |  |  | RW |  |  | Power Factor Reversion Enable (W Inj) | Power factor reversion timer when injecting active power enable.
704 | DER AC controls model. |  |  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
704 | DER AC controls model. |  |  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
704 | DER AC controls model. | 4 |  | PFWInjRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | PF Reversion Time (W Inj) | Power factor reversion timer when injecting active power.
704 | DER AC controls model. | 6 |  | PFWInjRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | PF Reversion Time Rem (W Inj) | Power factor reversion time remaining when injecting active power.
704 | DER AC controls model. | Set Power Factor (when absorbing active power)
704 | DER AC controls model. | 8 |  | PFWAbsEna |  |  | enum16 |  |  |  | RW |  |  | Power Factor Enable (W Abs) Enable | Power factor enable when absorbing active power.
704 | DER AC controls model. |  |  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
704 | DER AC controls model. |  |  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
704 | DER AC controls model. | 9 |  | PFWAbsEnaRvrt |  |  | enum16 |  |  |  | RW |  |  | Power Factor Reversion Enable (W Abs) | Power factor reversion timer when absorbing active power enable.
704 | DER AC controls model. |  |  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
704 | DER AC controls model. |  |  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
704 | DER AC controls model. | 10 |  | PFWAbsRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | PF Reversion Time (W Abs) | Power factor reversion timer when absorbing active power.
704 | DER AC controls model. | 12 |  | PFWAbsRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | PF Reversion Time Rem (W Abs) | Power factor reversion time remaining when absorbing active power.
704 | DER AC controls model. | Limit Maximum Active Power Generation
704 | DER AC controls model. | 14 |  | WMaxLimPctEna |  |  | enum16 |  |  |  | RW |  |  | Limit Max Power Pct Enable | Limit maximum active power percent enable.
704 | DER AC controls model. |  |  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
704 | DER AC controls model. |  |  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
704 | DER AC controls model. | 15 |  | WMaxLimPct |  |  | uint16 |  | WMaxLimPct_SF | Pct | RW |  |  | Limit Max Power Pct Setpoint | Limit maximum active power percent value.
704 | DER AC controls model. | 16 |  | WMaxLimPctRvrt |  |  | uint16 |  | WMaxLimPct_SF | Pct | RW |  |  | Reversion Limit Max Power Pct | Reversion limit maximum active power percent value.
704 | DER AC controls model. | 17 |  | WMaxLimPctEnaRvrt |  |  | enum16 |  |  |  | RW |  |  | Reversion Limit Max Power Pct Enable | Reversion limit maximum active power percent value enable.
704 | DER AC controls model. |  |  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
704 | DER AC controls model. |  |  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
704 | DER AC controls model. | 18 |  | WMaxLimPctRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Limit Max Power Pct Reversion Time | Limit maximum active power percent reversion time.
704 | DER AC controls model. | 20 |  | WMaxLimPctRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Limit Max Power Pct Rev Time Rem | Limit maximum active power percent reversion time remaining.
704 | DER AC controls model. | Set Active Power Level (may be negative for charging)
704 | DER AC controls model. | 22 |  | WSetEna |  |  | enum16 |  |  |  | RW |  |  | Set Active Power Enable | Set active power enable.
704 | DER AC controls model. |  |  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
704 | DER AC controls model. |  |  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
704 | DER AC controls model. | 23 |  | WSetMod |  |  | enum16 |  |  |  | RW |  |  | Set Active Power Mode | Set active power mode.
704 | DER AC controls model. |  |  | W_MAX_PCT | 0 | [8 empty] | Active Power As Max Percent | Active power setting is percentage of maximum active power.
704 | DER AC controls model. |  |  | WATTS | 1 | [8 empty] | Active Power As Watts | Active power setting is in watts.
704 | DER AC controls model. | 24 |  | WSet |  |  | int32 |  | WSet_SF | W | RW |  |  | Active Power Setpoint (W) | Active power setting value in watts.
704 | DER AC controls model. | 26 |  | WSetRvrt |  |  | int32 |  | WSet_SF | W | RW |  |  | Reversion Active Power (W) | Reversion active power setting value in watts.
704 | DER AC controls model. | 28 |  | WSetPct |  |  | int16 |  | WSetPct_SF | Pct | RW |  |  | Active Power Setpoint (Pct) | Active power setting value as percent.
704 | DER AC controls model. | 29 |  | WSetPctRvrt |  |  | int16 |  | WSetPct_SF | Pct | RW |  |  | Reversion Active Power (Pct) | Reversion active power setting value as percent.
704 | DER AC controls model. | 30 |  | WSetEnaRvrt |  |  | enum16 |  |  |  | RW |  |  | Reversion Active Power Enable | Reversion active power function enable.
704 | DER AC controls model. |  |  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
704 | DER AC controls model. |  |  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
704 | DER AC controls model. | 31 |  | WSetRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Active Power Reversion Time | Set active power reversion time.
704 | DER AC controls model. | 33 |  | WSetRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Active Power Rev Time Rem | Set active power reversion time remaining.
704 | DER AC controls model. | Set Reacitve Power Level
704 | DER AC controls model. | 35 |  | VarSetEna |  |  | enum16 |  |  |  | RW |  |  | Set Reactive Power Enable | Set reactive power enable.
704 | DER AC controls model. |  |  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
704 | DER AC controls model. |  |  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
704 | DER AC controls model. | 36 |  | VarSetMod |  |  | enum16 |  |  |  | RW |  |  | Set Reactive Power Mode | Set reactive power mode.
704 | DER AC controls model. |  |  | W_MAX_PCT | 0 | [8 empty] | Reactive Power As Watt Max Pct | Reactive power setting is percent of maximum active power.
704 | DER AC controls model. |  |  | VAR_MAX_PCT | 1 | [8 empty] | Reactive Power As Var Max Pct | Reactive power setting is percent of maximum reactive power.
704 | DER AC controls model. |  |  | VAR_AVAIL_PCT | 2 | [8 empty] | Reactive Power As Var Avail Pct | Reactive power setting is percent of available reactive power.
704 | DER AC controls model. |  |  | VA_MAX_PCT | 3 | [8 empty] | Reactive Power As VA Max Pct | Reactive power setting is percent of maximum apparent power.
704 | DER AC controls model. |  |  | VARS | 4 | [8 empty] | Reactive Power As Vars | Reactive power is in vars.
704 | DER AC controls model. | 37 |  | VarSetPri |  |  | enum16 |  |  |  | RW |  |  | Reactive Power Priority | Reactive power priority.
704 | DER AC controls model. |  |  | ACTIVE | 0 | [8 empty] | Active Power Priority | Active power priority.
704 | DER AC controls model. |  |  | REACTIVE | 1 | [8 empty] | Reactive Power Priority | Reactive power priority.
704 | DER AC controls model. |  |  | VENDOR | 2 | [8 empty] | Vendor Power Priority | Power priority is vendor specific mode.
704 | DER AC controls model. | 38 |  | VarSet |  |  | int32 |  | VarSet_SF | Var | RW |  |  | Reactive Power Setpoint (Vars) | Reactive power setting value in vars.
704 | DER AC controls model. | 40 |  | VarSetRvrt |  |  | int32 |  | VarSet_SF | Var | RW |  |  | Reversion Reactive Power (Vars) | Reversion reactive power setting value in vars.
704 | DER AC controls model. | 42 |  | VarSetPct |  |  | int16 |  | VarSetPct_SF | Pct | RW |  |  | Reactive Power Setpoint (Pct) | Reactive power setting value as percent.
704 | DER AC controls model. | 43 |  | VarSetPctRvrt |  |  | int16 |  | VarSetPct_SF | Pct | RW |  |  | Reversion Reactive Power (Pct) | Reversion reactive power setting value as percent.
704 | DER AC controls model. | 44 |  | VarSetEnaRvrt |  |  | enum16 |  |  |  | RW |  |  | Reversion Reactive Power Enable | Reversion reactive power function enable.
704 | DER AC controls model. |  |  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
704 | DER AC controls model. |  |  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
704 | DER AC controls model. | 45 |  | VarSetRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Reactive Power Reversion Time | Set reactive power reversion time.
704 | DER AC controls model. | 47 |  | VarSetRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Reactive Power Rev Time Rem | Set reactive power reversion time remaining.
704 | DER AC controls model. | Ramp Rate
704 | DER AC controls model. | 49 |  | WRmp |  |  | uint16 |  |  | %Max/Sec | RW |  |  | Normal Ramp Rate | Ramp rate for increases in active power during normal generation.
704 | DER AC controls model. | 50 |  | WRmpRef |  |  | enum16 |  |  |  | RW |  |  | Normal Ramp Rate Reference | Ramp rate reference unit for increases in active power or current during normal generation.
704 | DER AC controls model. |  |  | A_MAX | 0 | [8 empty] | Max Current Ramp | Ramp based on percent of max current per second.
704 | DER AC controls model. |  |  | W_MAX | 1 | [8 empty] | Max Active Power Ramp | Ramp based on percent of max active power per second.
704 | DER AC controls model. | 51 |  | VarRmp |  |  | uint16 |  |  | %Max/Sec | RW |  |  | Reactive Power Ramp Rate | Ramp rate based on max reactive power per second.
704 | DER AC controls model. | 52 |  | AntiIslEna |  |  | enum16 |  |  |  | RW |  |  | Anti-Islanding Enable | Anti-islanding enable.
704 | DER AC controls model. |  |  | DISABLED | 0 | [8 empty] | Disabled | Anti-islanding is disabled.
704 | DER AC controls model. |  |  | ENABLED | 1 | [8 empty] | Enabled | Anti-islanding is enabled.
704 | DER AC controls model. | Scale Factors
704 | DER AC controls model. | 53 |  | PF_SF |  |  | sunssf | [5 empty] | S | Power Factor Scale Factor | Power factor scale factor.
704 | DER AC controls model. | 54 |  | WMaxLimPct_SF |  |  | sunssf | [5 empty] | S | Limit Max Power Scale Factor | Limit maximum power scale factor.
704 | DER AC controls model. | 55 |  | WSet_SF |  |  | sunssf | [5 empty] | S | Active Power Scale Factor | Active power scale factor.
704 | DER AC controls model. | 56 |  | WSetPct_SF |  |  | sunssf | [5 empty] | S | Active Power Pct Scale Factor | Active power pct scale factor.
704 | DER AC controls model. | 57 |  | VarSet_SF |  |  | sunssf | [5 empty] | S | Reactive Power Scale Factor | Reactive power scale factor.
704 | DER AC controls model. | 58 |  | VarSetPct_SF |  |  | sunssf | [5 empty] | S | Reactive Power Pct Scale Factor | Reactive power pct scale factor.
704 | DER AC controls model. | Power Factor Settings
704 | DER AC controls model. |  |  | DERCtlAC.PFWInj |  |  | sync | [6 empty] | Power Factor (W Inj) | Power factor setpoint when injecting active power.
704 | DER AC controls model. |  | 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Power Factor (W Inj) | Power factor setpoint when injecting active power.
704 | DER AC controls model. |  | 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Power Factor Excitation (W Inj) | Power factor excitation setpoint when injecting active power.
704 | DER AC controls model. |  |  | OVER_EXCITED | 0 | [8 empty] | Over-Excited | Power factor over-excited excitation.
704 | DER AC controls model. |  |  | UNDER_EXCITED | 1 | [8 empty] | Under-Excited | Power factor under-excited excitation.
704 | DER AC controls model. |  |  | DERCtlAC.PFWInjRvrt |  |  | sync | [6 empty] | Reversion Power Factor (W Inj) | Reversion power factor setpoint when injecting active power.
704 | DER AC controls model. |  | 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Reversion Power Factor (W Inj) | Reversion power factor setpoint when injecting active power.
704 | DER AC controls model. |  | 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Reversion PF Excitation (W Inj) | Reversion power factor excitation setpoint when injecting active power.
704 | DER AC controls model. |  |  | OVER_EXCITED | 0 | [8 empty] | Over-Excited | Power factor over-excited excitation.
704 | DER AC controls model. |  |  | UNDER_EXCITED | 1 | [8 empty] | Under-Excited | Power factor under-excited excitation.
704 | DER AC controls model. |  |  | DERCtlAC.PFWAbs |  |  | sync | [6 empty] | Power Factor (W Abs) | Power factor setpoint when absorbing active power.
704 | DER AC controls model. |  | 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Power Factor (W Abs) | Power factor setpoint when absorbing active power.
704 | DER AC controls model. |  | 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Power Factor Excitation (W Abs) | Power factor excitation setpoint when absorbing active power.
704 | DER AC controls model. |  |  | OVER_EXCITED | 0 | [8 empty] | Over-Excited | Power factor over-excited excitation.
704 | DER AC controls model. |  |  | UNDER_EXCITED | 1 | [8 empty] | Under-Excited | Power factor under-excited excitation.
704 | DER AC controls model. |  |  | DERCtlAC.PFWAbsRvrt |  |  | sync | [6 empty] | Reversion Power Factor (W Abs) | Reversion power factor setpoint when absorbing active power.
704 | DER AC controls model. |  | 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Reversion Power Factor (W Abs) | Reversion power factor setpoint when absorbing active power.
704 | DER AC controls model. |  | 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Reversion PF Excitation (W Abs) | Reversion power factor excitation setpoint when absorbing active power.
704 | DER AC controls model. |  |  | OVER_EXCITED | 0 | [8 empty] | Over-Excited | Power factor over-excited excitation.
704 | DER AC controls model. |  |  | UNDER_EXCITED | 1 | [8 empty] | Under-Excited | Power factor under-excited excitation.
705-712: Inverter control settings, coming later
713 | DER Storage Capacity | 2 |  | WHRtg |  |  | uint16 |  | WH_SF | WH |  |  |  | Energy Rating | Energy rating of the DER storage.
713 | DER Storage Capacity | 3 |  | WHAvail |  |  | uint16 |  | WH_SF | WH |  |  |  | Energy Available | Energy available of the DER storage (WHAvail = WHRtg * SoC * SoH)
713 | DER Storage Capacity | 4 |  | SoC |  |  | uint16 |  | Pct_SF | Pct |  |  |  | State of Charge | State of charge of the DER storage.
713 | DER Storage Capacity | 5 |  | SoH |  |  | uint16 |  | Pct_SF | Pct |  |  |  | State of Health | State of health of the DER storage.
713 | DER Storage Capacity | 6 |  | Sta |  |  | enum16 | [6 empty] | Status | Storage status.
713 | DER Storage Capacity |  |  | OK | 0 | [8 empty] | OK | No warnings or errors pending.
713 | DER Storage Capacity |  |  | WARNING | 1 | [8 empty] | Warning | One or more warnings pending.
713 | DER Storage Capacity |  |  | ERROR | 2 | [8 empty] | Error | One or more errors pending.
713 | DER Storage Capacity | 7 |  | WH_SF |  |  | sunssf | [5 empty] | S | Energy Scale Factor | Scale factor for energy capacity.
713 | DER Storage Capacity | 8 |  | Pct_SF |  |  | sunssf | [5 empty] | S | Percent Scale Factor | Scale factor for percentage.
714 | DER DC Measurement | DC General
714 | DER DC Measurement | 2 |  | PrtAlrms |  |  | bitfield32 | [6 empty] | Port Alarms | Bitfield of ports with active alarms. Bit is 1 if port has an active alarm. Bit 0 is first port.
714 | DER DC Measurement | 4 |  | NPrt |  |  | uint16 | [5 empty] | S | Number Of Ports | Number of DC ports.
714 | DER DC Measurement | 5 |  | DCA |  |  | int16 |  | DCA_SF | A |  |  |  | DC Current | Total DC current for all ports.
714 | DER DC Measurement | 6 |  | DCW |  |  | int16 |  | DCW_SF | W |  |  |  | DC Power | Total DC power for all ports.
714 | DER DC Measurement | 7 |  | DCWhInj |  |  | uint64 |  | DCWH_SF | Wh |  |  |  | DC Energy Injected | Total cumulative DC energy injected for all ports.
714 | DER DC Measurement | 11 |  | DCWhAbs |  |  | uint64 |  | DCWH_SF | Wh |  |  |  | DC Energy Absorbed | Total cumulative DC energy absorbed for all ports.
714 | DER DC Measurement | 15 |  | DCA_SF |  |  | sunssf | [5 empty] | S | DC Current Scale Factor | DC current scale factor.
714 | DER DC Measurement | 16 |  | DCV_SF |  |  | sunssf | [5 empty] | S | DC Voltage Scale Factor | DC voltage scale factor.
714 | DER DC Measurement | 17 |  | DCW_SF |  |  | sunssf | [5 empty] | S | DC Power Scale Factor | DC power scale factor.
714 | DER DC Measurement | 18 |  | DCWH_SF |  |  | sunssf | [5 empty] | S | DC Energy Scale Factor | DC energy scale factor.
714 | DER DC Measurement | 19 |  | Tmp_SF |  |  | sunssf | [5 empty] | S | Temperature Scale Factor | Temperature Scale Factor.
714 | DER DC Measurement | DC Port
714 | DER DC Measurement |  |  | DERMeasureDC.Prt |  | NPrt | group
714 | DER DC Measurement |  | 0 | PrtTyp |  |  | enum16 | [6 empty] | Port Type | Port type.
714 | DER DC Measurement |  |  | PV | 0 | [8 empty] | Photovoltaic
714 | DER DC Measurement |  |  | ESS | 1 | [8 empty] | Energy Storage System
714 | DER DC Measurement |  |  | EV | 2 | [8 empty] | Electric Vehicle
714 | DER DC Measurement |  |  | INJ | 3 | [8 empty] | Generic Injecting
714 | DER DC Measurement |  |  | ABS | 4 | [8 empty] | Generic Absorbing
714 | DER DC Measurement |  |  | BIDIR | 5 | [8 empty] | Generic Bidirectional
714 | DER DC Measurement |  |  | DC_DC | 6 | [8 empty] | DC to DC
714 | DER DC Measurement |  | 1 | ID |  |  | uint16 | [6 empty] | Port ID | Port ID.
714 | DER DC Measurement |  | 2 | IDStr |  |  | string | 8 | [5 empty] | Port ID String | Port ID string.
714 | DER DC Measurement |  | 10 | DCA |  |  | int16 |  | DCA_SF | A |  |  |  | DC Current | DC current for the port.
714 | DER DC Measurement |  | 11 | DCV |  |  | uint16 |  | DCV_SF | V |  |  |  | DC Voltage | DC voltage for the port.
714 | DER DC Measurement |  | 12 | DCW |  |  | int16 |  | DCW_SF | W |  |  |  | DC Power | DC power for the port.
714 | DER DC Measurement |  | 13 | DCWhInj |  |  | uint64 |  | DCWH_SF | Wh |  |  |  | DC Energy Injected | Total cumulative DC energy injected for the port.
714 | DER DC Measurement |  | 17 | DCWhAbs |  |  | uint64 |  | DCWH_SF | Wh |  |  |  | DC Energy Absorbed | Total cumulative DC energy absorbed for the port.
714 | DER DC Measurement |  | 21 | Tmp |  |  | int16 |  | Tmp_SF | C |  |  |  | DC Port Temperature | DC port temperature.
714 | DER DC Measurement |  | 22 | DCSta |  |  | enum16 | [6 empty] | DC Port Status | DC port status.
714 | DER DC Measurement |  |  | OFF | 0 | [8 empty] | Off
714 | DER DC Measurement |  |  | ON | 1 | [8 empty] | On
714 | DER DC Measurement |  |  | WARNING | 2 | [8 empty] | Warning
714 | DER DC Measurement |  |  | ERROR | 3 | [8 empty] | Error
714 | DER DC Measurement |  | 23 | DCAlrm |  |  | bitfield32 | [6 empty] | DC Port Alarm | DC port alarm.
714 | DER DC Measurement |  |  | GROUND_FAULT | 0 | [8 empty] | Ground Fault
714 | DER DC Measurement |  |  | INPUT_OVER_VOLTAGE | 1 | [8 empty] | Input Over Voltage
714 | DER DC Measurement |  |  | DC_DISCONNECT | 3 | [8 empty] | DC Disconnect
714 | DER DC Measurement |  |  | CABINET_OPEN | 5 | [8 empty] | Cabinet Open
714 | DER DC Measurement |  |  | MANUAL_SHUTDOWN | 6 | [8 empty] | Manual Shutdown
714 | DER DC Measurement |  |  | OVER_TEMP | 7 | [8 empty] | Over Temperature
714 | DER DC Measurement |  |  | BLOWN_FUSE | 12 | [8 empty] | Blown Fuse
714 | DER DC Measurement |  |  | UNDER_TEMP | 13 | [8 empty] | Under Temperature
714 | DER DC Measurement |  |  | MEMORY_LOSS | 14 | [8 empty] | Memory Loss
714 | DER DC Measurement |  |  | ARC_DETECTION | 15 | [8 empty] | Arc Detection
714 | DER DC Measurement |  |  | RESERVED | 19 | [8 empty] | Reserved
714 | DER DC Measurement |  |  | TEST_FAILED | 20 | [8 empty] | Test Failed
714 | DER DC Measurement |  |  | INPUT_UNDER_VOLTAGE | 21 | [8 empty] | Under Voltage
714 | DER DC Measurement |  |  | INPUT_OVER_CURRENT | 22 | [8 empty] | Over Current
715 | DERCtl | DER Controls
715 | DERCtl | 2 |  | LocRemCtl |  |  | enum16 | [6 empty] | Control Mode | DER control mode. Enumeration.
715 | DERCtl |  |  | REMOTE | 0 | [8 empty] | Remote Control
715 | DERCtl |  |  | LOCAL | 1 | [8 empty] | Local Control | Local mode is required for manual/maintenance operations. Once invoked, it must be explicitly exited for the inverter to be controlled remotely.
715 | DERCtl | 3 |  | DERHb |  |  | uint32 | [6 empty] | DER Heartbeat | Value is incremented every second by the DER with periodic resets to zero.
715 | DERCtl | 5 |  | ControllerHb |  |  | uint32 |  |  |  | RW |  |  | Controller Heartbeat | Value is incremented every second by the controller with periodic resets to zero.
715 | DERCtl | 7 |  | AlarmReset |  |  | uint16 |  |  |  | RW |  |  | Alarm Reset | Used to reset any latched alarms. 1 = Reset.
715 | DERCtl | 8 |  | OpCtl |  |  | enum16 |  |  |  | RW |  |  | Set Operation | Commands to PCS. Enumerated value.
715 | DERCtl |  |  | STOP | 0 | [8 empty] | Stop the DER
715 | DERCtl |  |  | START | 1 | [8 empty] | Start the DER
715 | DERCtl |  |  | ENTER_STANDBY | 2 | [8 empty] | Enter Standby Mode
715 | DERCtl |  |  | EXIT_STANDBY | 3 | [8 empty] | Exit Standby Mode