## Note
Some important notes
we leave out the inlanding parameters, calculation relevant settings and test settings
no calculation and data transfer inside the data model
Beh, Mod, Health not specified, we don't play around with these settings. These nodes will be automatically created during model generation, as they are mandatory nodes, but they will not be listed in the matching table.
no use of mixed DER, if it is the case, consider them separately
emergency mode is not considered
Autorization and authentification provided by Smart-Meter-Infrastructure
All controllable resources are fully controllable
DER completely shut down will not be an option in our case, instead use Wmax and other settings to limit the active/reactive power. -> we do not actively connect or disconnect the DER to/from the grid
Over-/underexciting ratings and settings are not considered
switching between interconnected and not interconnected to the grid is not considered, assume that the DER is always interconnected
No autonomous operational functions -> we always assume that Mod.stVal = 1 (On), and Beh in LN also stays at 1
possibly reduce the usage of ORG and other reference parameters for simplicity
virtual power plant, aggregation is not yet considered (the LN DVER is not in use)
not strictly refering to the presece condition defined in IEC-61850
most of the DA in LN DINV could be replaced by the same ones in LN DGEN

## DGEN
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of external (electrical, mechanical or communication) equipment to which the logical node is associated. | Descriptions |  | DGEN | EEName | DPL
Name plate of the logical node. | Descriptions |  | DGEN | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | DGEN | Beh | ENS | BehaviourModeKind
Reflects the state of the logical node related hardware and software. More detailed information related to the source of the problem may be provided by specific attribute of the logical node. | Status information |  | DGEN | Health | ENS | HealthKind
If true, the operation of the whole logical device has been switched (from remote) to local. | Status information |  | DGEN | LocKey | SPS
If true, the control behaviour is allowed at this level. | Status information |  | DGEN | Loc | SPS
Synchronization status of the DER generator unit. | Status information |  | DGEN | GnSynSt | ENS | DERSynchronizationKind
Current state of operation of the distributed energy resource. | Status information |  | DGEN | DEROpSt | ENS | DERStateKind
Operation time of the external (electrical, mechanical or communication) equipment since start of the operation. | Status information |  | DGEN | OpTmh | INS
State of external (electrical, mechanical or communication) equipment to which the logical node is associated. | Status information |  | DGEN | EEHealth | ENS | HealthKind
The calculation of the maximum power that the generator could output, based on constraining environmental conditions (e.g. solar insolation or wind speed or constraints from heat or vibrations). The delta between this calculation and the actual power being output indicates how much additional power could be output. | Measured and metered values |  | DGEN | CnstWMax | MV
Total energy generated | Measured and metered values |  | DGEN | GnEnTot | MV
Energy generated during the period since last reset | Measured and metered values |  | DGEN | GnEnPer | MV
Percentage of the active power currently generated which results from renewable energy resource. What is considered as renewable is a local definition. | Measured and metered values |  | DGEN | RenWPct | MV
Percentage of the reactive power currently generated which results from renewable energy resource. What is considered as renewable is a local definition. | Measured and metered values |  | DGEN | RenVArPct | MV
The total amount of reactive power without impacting active power output if the distinction between absorbing and injecting reactive power is not significant (the use of this DO is mutually exclusive with the use of AvarTot and IvarTot) | Measured and metered values |  | DGEN | VArTot | MV
The total amount of reactive power available for absorbing even if possibly impacting active power output (the use of this DO is mutually exclusive with the use of VArTot) | Measured and metered values |  | DGEN | AvarTot | MV
The total amount of reactive power available for injecting even if possibly impacting active power output (the use of this DO is mutually exclusive with the use of VArTot) | Measured and metered values |  | DGEN | IvarTot | MV
The amount of reactive power available without impacting active power output if the distinction between absorbing and injecting reactive power is not significant (the use of this DO is mutually exclusive with the use of AvarAvl and IvarAvl) | Measured and metered values |  | DGEN | VArAvl | MV
The amount of reactive power available for absorbing without impacting active power output (the use of this DO is mutually exclusive with the use of VArAvl) | Measured and metered values |  | DGEN | AvarAvl | MV
The amount of reactive power available for injecting without impacting active power output (the use of this DO is mutually exclusive with the use of VArAvl) | Measured and metered values |  | DGEN | IvarAvl | MV
Actual self service energy used | Measured and metered values |  | DGEN | SelfSvcWh | MV
Actual percentage of apparent power output based on VAMax | Measured and metered values |  | DGEN | VAPct | MV
Available capability (measured or calculated) for increasing active output, including increasing generation of active power, even if currently consuming power. | Measured and metered values |  | DGEN | AvlUpW | MV
Available capability (measured or calculated) for decreasing active power, including increasing the consumption of active power, even if currently generating power. | Measured and metered values |  | DGEN | AvlDnW | MV
(controllable) Operating mode of the domain logical node that may be changed by operator. | Controls |  | DGEN | Mod | ENC | BehaviourModeKind
(controllable) If true, control authority is at station level and control from remote is disabled; otherwise control from remote is allowed. | Controls |  | DGEN | LocSta | SPC
The number of times that the DER unit has been turned on or returned to service: count of "DER unit on" times, since the last time the counter was reset | Controls |  | DGEN | GnOnCnt | INC
Count of total number of starts | Controls |  | DGEN | TotStrCnt | INC
Count of starts in period since reset | Controls |  | DGEN | PerStrCnt | INC
Total time DER unit has operated – resettable: accumulated time since the last time the time was reset | Controls |  | DGEN | OpTms | INC
Reset the generated energy in period | Controls |  | DGEN | GnEnPerRs | SPC
(controllable) Operating with the value expressed in ctlVal (selected among the list specified in DERStateControlKind) initiates the appropriate transition request. The reading of its attribute stVal is meaningless. The resulting state of the DER shall be observed in the DEROpSt DO. | Controls |  | DGEN | DEROpStCtl | ENC | DERStateTransitionKind
Active power setpoint. Its mxVal attribute reflects the value of the setpoint that is requested. | Controls |  | DGEN | WSpt | APC
Reactive power setpoint. Its mxVal attribute reflects the value of the setpoint that is requested. | Controls |  | DGEN | VArSpt | APC
Active power setpoint (deprecated) | Controls |  | DGEN | OutWSet | ASG
Reactive power setpoint (deprecated) | Controls |  | DGEN | OutVarSet | ASG
(controllable) Operations count, can be reset to a value different than 0. | Controls |  | DGEN | OpCntRs | INC
Included generator. This DO points to an instance of DGEN | Settings |  | DGEN | InclGn | ORG
Nameplate maximum active generation power rating at unity power factor | Settings |  | DGEN | WMaxRtg | ASG
Nameplate maximum apparent power generation rating | Settings |  | DGEN | VAMaxRtg | ASG
Setpoint for maximum reactive power if the distinction between absorbing and injecting reactive power is not significant | Settings |  | DGEN | VArMaxRtg | ASG
Rating for maximum absorbing reactive power | Settings |  | DGEN | AvarMaxRtg | ASG
Rating for maximum supply (injection) reactive power | Settings |  | DGEN | IvarMaxRtg | ASG
Maximum current rating under nominal voltage under nominal power factor | Settings |  | DGEN | AMaxRtg | ASG
Maximum voltage rating | Settings |  | DGEN | VMaxRtg | ASG
Minimum voltage rating | Settings |  | DGEN | VMinRtg | ASG
Maximum generation active power ramp up rating | Settings |  | DGEN | WRpuMaxRtg | ASG
Maximum generation active power ramp down rating | Settings |  | DGEN | WRpdMaxRtg | ASG
Max rated active power (WMaxRtg) which may result from controllable resource, .i.e whose level can be potentially controlled/set under the request of an entity external to the given DER. | Settings |  | DGEN | CtbWMaxRtg | ASG
Max rated reactive power VArMaxRtg, which may result from controllable resource, .i.e whose level can be potentially controlled/set under the request of an entity external to the given DER. | Settings |  | DGEN | CtbVArMaxRtg | ASG
Setting for maximum active power | Settings |  | DGEN | WMax | ASG
Default ramp rate for changes in active power: percentage of WMax per second | Settings |  | DGEN | WRmp | ASG
Setting for maximum reactive power if the distinction between absorbing and injecting reactive power is not significant (the use of this DO is mutually exclusive with the use of AvarMax and IvarMax) | Settings |  | DGEN | VArMax | ASG
Setting for maximum absorbing reactive power (the use of this DO is mutually exclusive with the use of VArMax) | Settings |  | DGEN | AvarMax | ASG
Setting for maximum supply (injection) reactive power (the use of this DO is mutually exclusive with the use of VArMax) | Settings |  | DGEN | IvarMax | ASG
Setting for maximum voltage operational rating | Settings |  | DGEN | VMax | ASG
Setting for minimum voltage operational rating | Settings |  | DGEN | VMin | ASG
Setting for maximum operational current rating under nominal voltage under nominal power factor | Settings |  | DGEN | AMax | ASG
Setting for maximum apparent power while generating (the use of this DO is mutually exclusive with the use of AvaMax and IvaMax) | Settings |  | DGEN | VAMax | ASG
Setting for maximum absorbing apparent power (the use of this DO is mutually exclusive with the use of VAMax) | Settings |  | DGEN | AvaMax | ASG
Setting for maximum injecting apparent power (the use of this DO is mutually exclusive with the use of VAMax) | Settings |  | DGEN | IvaMax | ASG
Reference for reactive power setpoints. Selects which setpoint is active. | Settings |  | DGEN | VArSptRef | ENG | ReactivePowerRefParamKind
Connection type of ECP: connection to DER (Point of Connection (PoC)), to load, within Local Electric Power System (Local EPS), Point of Common Coupling (PCC), or directly to Area EPS | Settings |  | DGEN | EcpConnTyp | ENG | ECPConnKind
Phase type of electrical connection of the DER | Settings |  | DGEN | PhsConnTyp | ENG | PhaseKind
Type of DER | Settings |  | DGEN | DERTyp | ENG | DERUnitKind
Maximum temperature rating | Settings |  | DGEN | TmpMaxRtg | ASG
Selfservice nominal power | Settings |  | DGEN | SelfWRtg | ASG
Selfservice voltage | Settings |  | DGEN | SelfVRtg | ASG
Selfservice nominal power factor | Settings |  | DGEN | SelfPFRtg | ASG
Sequence (direction) reversed: False = ABC, true = CBA | Settings |  | DGEN | RvSeq | SPG
Selfservice acceptable voltage range | Settings |  | DGEN | SelfVRngRtg | ASG
Efficiency at rated capacity as percent | Settings |  | DGEN | EfcRtgPct | ASG
Rated Nominal frequency of usage of the DER | Settings |  | DGEN | HzNomRtg | ASG
Rated minimal frequency of usage of the DER | Settings |  | DGEN | HzMinRtg | ASG
Rated maximum frequency of usage of the DER | Settings |  | DGEN | HzMaxRtg | ASG
Internal identifier of the resource within a system which is using that resource. It complements the mRID defined as part of the EEname DO. Different DERIds may be defined for different system users. | Settings |  | DGEN | DERId | VSG

## DSTO
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of external (electrical, mechanical or communication) equipment to which the logical node is associated. | Descriptions |  | DSTO | EEName | DPL
Name plate of the logical node. | Descriptions |  | DSTO | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | DSTO | Beh | ENS | BehaviourModeKind
Reflects the state of the logical node related hardware and software. More detailed information related to the source of the problem may be provided by specific attribute of the logical node. | Status information |  | DSTO | Health | ENS | HealthKind
If true, the operation of the whole logical device has been switched (from remote) to local. | Status information |  | DSTO | LocKey | SPS
If true, the control behaviour is allowed at this level. | Status information |  | DSTO | Loc | SPS
Alarm trigger status: if true, the maximum state of charge threshold of the battery (SocHiAlsPct) has been exceeded | Status information |  | DSTO | SocHiAlm | SPS
Warning trigger status: if true, the high state of charge warning threshold of the battery has been exceeded | Status information |  | DSTO | SocHiWrn | SPS
Alarm trigger status: If true,the minimum state of charge threshold of the battery (SocLoAlsPct) has been exceeded | Status information |  | DSTO | SocLoAlm | SPS
Warning trigger status: if true, the low state of charge warning threshold of the battery has been exceeded | Status information |  | DSTO | SocLoWrn | SPS
Alarm trigger status: If true, the predefined threshold of the low state of health of the storage resource (SohLoAlsPct) has been reached | Status information |  | DSTO | SohLoAlm | SPS
Count of the number of equivalent full charge cycles | Status information |  | DSTO | ChaCycCnt | INS
Current state of operation of the distributed energy resource. | Status information |  | DSTO | DEROpSt | ENS | DERStateKind
State of external (electrical, mechanical or communication) equipment to which the logical node is associated. | Status information |  | DSTO | EEHealth | ENS | HealthKind
Operation time of the external (electrical,mechanical or communication) equipment sincestart of the operation. | Status information |  | DSTO | OpTmh | INS
Available energy capacity to be charged (in Wh) | Measured and metered values |  | DSTO | InWh | MV
Energy stored and available for discharging (in Wh) | Measured and metered values |  | DSTO | OutWh | MV
state of charge expressed in Wh | Measured and metered values |  | DSTO | SocWh | MV
Usable state of charge (expressed as percent of total usable energy capacity UseWh) which may be directly measured or calculated | Measured and metered values |  | DSTO | UseSocPct | MV
State of charge as percentage in relation to the effective energy capacity of the storage resource with respect to the degradation so far (EffWh). | Measured and metered values |  | DSTO | SocEffWhPct | MV
Total Energy Charged since last reset (in Wh) | Measured and metered values |  | DSTO | ChaWhTot | MV
Total Energy Discharged since last reset | Measured and metered values |  | DSTO | DschWhTot | MV
Available power | Measured and metered values |  | DSTO | AvlDschW | MV
Available charging power | Measured and metered values |  | DSTO | AvlChaW | MV
Actual volt-amps percentage charged based on ChaVAMax | Measured and metered values |  | DSTO | ChaVAPct | MV
available charging time | Measured and metered values |  | DSTO | AvlChaWTm | MV
Available discharging time | Measured and metered values |  | DSTO | AvlDschWTm | MV
The total amount of reactive power available for absorbing even if possibly impacting active power output while charging | Measured and metered values |  | DSTO | ChaAvarTot | MV
The total amount of reactive power available for absorbing even if possibly impacting active power output while discharging. | Measured and metered values |  | DSTO | DschAvarTot | MV
The total amount of reactive power available for injecting even if possibly impacting active power output while charging | Measured and metered values |  | DSTO | ChaIvarTot | MV
The total amount of reactive power available for injecting even if possibly impacting active power output while discharging | Measured and metered values |  | DSTO | DschIvarTot | MV
The amount of reactive power available for absorbing without impacting active power output while charging | Measured and metered values |  | DSTO | ChaAvarAvl | MV
The amount of reactive power available for absorbing without impacting active power output while discharging | Measured and metered values |  | DSTO | DschAvarAvl | MV
The amount of reactive power available for injecting without impacting active power output while charging | Measured and metered values |  | DSTO | ChaIvarAvl | MV
The amount of reactive power available for injecting without impacting active power output while discharging | Measured and metered values |  | DSTO | DschIvarAvl | MV
Effective actual total energy capacity (in Wh) provided by the storage resource. Due to degradation, the amount may be less than the rated total energy capacity (WhRtg). | Measured and metered values |  | DSTO | EffWh | MV
Effective actual total energy capacity (expressed as percentage of WhRtg) provided by the storage resource. Due to degradation, the amount may be less than the rated total energy capacity (WhRtg). In case both WhEffCapPct and WhEffCap DOs are present in a same LN instance, the application shall ensure to keep the values of both DOs consistent. | Measured and metered values |  | DSTO | EffWhPct | MV
Actual self service energy used | Measured and metered values |  | DSTO | SelfSvcWh | MV
Actual percentage of apparent power output based on VAMax | Measured and metered values |  | DSTO | VAPct | MV
Available capability (measured or calculated) for increasing active output, including increasing generation of active power, even if currently consuming power. | Measured and metered values |  | DSTO | AvlUpW | MV
Available capability (measured or calculated) for decreasing active power, including increasing the consumption of active power, even if currently generating power. | Measured and metered values |  | DSTO | AvlDnW | MV
(controllable) Operating mode of the domain logical node that may be changed by operator. | Controls |  | DSTO | Mod | ENC | BehaviourModeKind
(controllable) If true, control authority is at station level and control from remote is disabled; otherwise control from remote is allowed. | Controls |  | DSTO | LocSta | SPC
Operating with the value expressed in ctlVal (selected among the list specified in DERStateControlKind) initiates the appropriate transition request. The reading of its attribute stVal is meaningless. The resulting state of the DER shall be observed in the DEROpSt DO. | Controls |  | DSTO | DEROpStCtl | ENC | DERStateTransitionKind
Active power setpoint. Its mxVal attribute reflects the value of the setpoint that is requested. | Controls |  | DSTO | WSpt | APC
Reactive power setpoint. Its mxVal attribute reflects the value of the setpoint that is requested. | Controls |  | DSTO | VArSpt | APC
Active power setpoint (deprecated) | Controls |  | DSTO | OutWSet | ASG
Reactive power setpoint (deprecated) | Controls |  | DSTO | OutVarSet | ASG
Operations count, can be reset to a value different than 0. | Controls |  | DSTO | OpCntRs | INC
Reference to the equivalent DSTO instance reflecting the generic storage aspects of the storage unit | Settings |  | DSTO | EqSto | ORG
Reference to the DER Unit LN which may be associated to this generic model LN | Settings |  | DSTO | DERUnit | ORG
High state of charge alarm threshold of the battery (in percent) | Settings |  | DSTO | SocHiAlsPct | ASG
Warning high state of charge threshold of the battery (in percent) | Settings |  | DSTO | SocHiWrsPct | ASG
Low state of charge alarm threshold of the battery (in percent) | Settings |  | DSTO | SocLoAlsPct | ASG
Warning state of charge threshold of the battery (in percent) | Settings |  | DSTO | SocLoWrsPct | ASG
Threshold alarm setting of the usable lower limit of the storage resource (in % of the usable capacity of the storage element (in Wh) – CapWhUseRtg ) | Settings |  | DSTO | SohLoAlsPct | ASG
Roundtrip efficiency [%] at nominal conditions | Settings |  | DSTO | RntEffPct | ASG
Nameplate maximum active power rating while charging | Settings |  | DSTO | ChaWMaxRtg | ASG
Nameplate maximum active power rating while discharging | Settings |  | DSTO | DschWMaxRtg | ASG
Nameplate ramp rate for changes in active power while charging: percentage of WMax per second | Settings |  | DSTO | ChaWRmpRtg | ASG
Nameplate ramp rate for changes in active power while discharging: percentage of WMax per second | Settings |  | DSTO | DschWRmpRtg | ASG
Nameplate maximum apparent charging power rating | Settings |  | DSTO | ChaVAMaxRtg | ASG
Nameplate maximum apparent discharging power rating | Settings |  | DSTO | DschVAMaxRtg | ASG
Nameplate rating for maximum absorbing reactive power while charging | Settings |  | DSTO | ChaAvarRtg | ASG
Nameplate rating for maximum absorbing reactive power while discharging | Settings |  | DSTO | DschAvarRtg | ASG
Nameplate rating for maximum supply (injection) reactive power while charging | Settings |  | DSTO | ChaIvarRtg | ASG
Nameplate rating for maximum supply (injection) reactive power while discharging | Settings |  | DSTO | DschIvarRtg | ASG
Nameplate rating for maximum voltage while charging | Settings |  | DSTO | ChaVMaxRtg | ASG
Nameplate rating for maximum voltage while discharging | Settings |  | DSTO | DschVMaxRtg | ASG
Nameplate rating for minimum voltage while charging | Settings |  | DSTO | ChaVMinRtg | ASG
Nameplate rating for minimum voltage while discharging | Settings |  | DSTO | DschVMinRtg | ASG
Nameplate rating for maximum current under nominal voltage under nominal power factor while charging | Settings |  | DSTO | ChaAMaxRtg | ASG
Nameplate rating for maximum current under nominal voltage under nominal power factor while discharging | Settings |  | DSTO | DschAMaxRtg | ASG
Nameplate energy storage capacity rating in Wh | Settings |  | DSTO | WhRtg | ASG
Nameplate maximum amount of energy (in Wh) to be stored in the storage resource for e.g. supporting long life and avoid faster degradation | Settings |  | DSTO | WhMaxRtg | ASG
Nameplate minimum amount of energy (in Wh) to be retained in the storage resource for e.g. supporting long life and avoid faster degradation or to ensure a reserve of energy stored for emergencies and other purposes. | Settings |  | DSTO | WhMinRtg | ASG
Charging efficiency curve rating [% over SoC] | Settings |  | DSTO | ChaEfcRtg | CSG
Discharging efficiency curve rating [% over SoC] | Settings |  | DSTO | DschEfcRtg | CSG
Net Energy Metering (NEM) Policy Mode which establishes whether the DER qualifies as renewable. Mode A = Storage may charge from the grid but may not discharge to the grid (acts only as load). Mode B = Storage may not charge from the grid but may discharge to the grid (charges from local energy source). Mode C = Storage may charge or discharge from the grid at will / in response to commands for location where there are no NEM integrity concerns. | Settings |  | DSTO | ChaSrcRtg | ENG | ChargeSourceKind
Maximum active power while charging | Settings |  | DSTO | ChaWMax | ASG
Default ramp rate for changes in active power: percentage of WMax per second while charging | Settings |  | DSTO | ChaWRmp | ASG
Default ramp rate for changes in active power: percentage of WMax per second while discharging | Settings |  | DSTO | DschWRmp | ASG
Maximum active power while discharging. (This DO is optional because WMax could be used) | Settings |  | DSTO | DschWMax | ASG
Charging reactive power maximum | Settings |  | DSTO | ChaVArMax | ASG
Discharging reactive power maximum | Settings |  | DSTO | DschVArMax | ASG
Maximum apparent charging power | Settings |  | DSTO | ChaVAMax | ASG
Operational setpoint for maximum apparent power while discharging | Settings |  | DSTO | DschVAMax | ASG
Operational setpoint for maximum absorbing reactive power while charging | Settings |  | DSTO | ChaAvarMax | ASG
Operational setpoint for maximum absorbing reactive power while discharging | Settings |  | DSTO | DschAvarMax | ASG
Operational setpoint for maximum supply (injection) reactive power while charging | Settings |  | DSTO | ChaIvarMax | ASG
Operational setpoint for maximum supply (injection) reactive power while discharging | Settings |  | DSTO | DschIvarMax | ASG
Operational setting for maximum voltage while charging | Settings |  | DSTO | ChaVMax | ASG
Operational setpoint for maximum voltage while discharging | Settings |  | DSTO | DschVMax | ASG
Operational setting for minimum voltage while charging | Settings |  | DSTO | ChaVMin | ASG
Operational setpoint for minimum voltage while discharging | Settings |  | DSTO | DschVMin | ASG
Operational setting for maximum current under nominal voltage under nominal power factor while charging | Settings |  | DSTO | ChaAMax | ASG
Operational setpoint for maximum current under nominal voltage under nominal power factor while discharging | Settings |  | DSTO | DschAMax | ASG
Charging efficiency curve [% over SoC] | Settings |  | DSTO | ChaEfc | CSG
Discharging efficiency curve [% over SoC] | Settings |  | DSTO | DschEfc | CSG
The energy reserve level above which the storage system may be only be charged in emergency situations, expressed as a percentage of the usable capacity, WhUseCap. | Settings |  | DSTO | UseWhMaxPct | ASG
The energy reserve level below which the storage system may be only be discharged in emergency situations, expressed as a percentage of the usable capacity, WhUseCap. | Settings |  | DSTO | UseWhMinPct | ASG
Operational setpoint for usable energy storage capacity in Wh | Settings |  | DSTO | UseWh | ASG
Net Energy Metering (NEM) Policy Mode which establishes whether the DER qualifies as renewable. Mode A = Storage may charge from the grid but may not discharge to the grid (acts only as load). Mode B = Storage may not charge from the grid but may discharge to the grid (charges from local energy source). Mode C = Storage may charge or discharge from the grid at will / in response to commands for location where there are no NEM integrity concerns. | Settings |  | DSTO | ChaSrc | ENG | ChargeSourceKind
Source of charging storage: True = charge from renewable sources only, False = charge from any sources | Settings |  | DSTO | RenChaEna | SPG
Reference to ECP directly connected at the output of the DER, the "plug" part. Note: The power management function ECP associated to this same resource will refer to the "socket" part. | Settings |  | DSTO | OutEcpRef | ORG
Connection type of ECP: connection to DER (Point of Connection (PoC)), to load, within Local Electric Power System (Local EPS), Point of Common Coupling (PCC), or directly to Area EPS | Settings |  | DSTO | EcpConnTyp | ENG | ECPConnKind
Phase type of electrical connection of the DER | Settings |  | DSTO | PhsConnTyp | ENG | PhaseKind
Type of DER | Settings |  | DSTO | DERTyp | ENG | DERUnitKind
Maximum temperature rating | Settings |  | DSTO | TmpMaxRtg | ASG
Exposure to fault rates as percent of ?? | Settings |  | DSTO | FltRtgPct | ASG
Max fault current rating | Settings |  | DSTO | FltAMaxRtg | ASG
Selfservice voltage | Settings |  | DSTO | SelfVRtg | ASG
Max fault duration rating | Settings |  | DSTO | FltDurMaxTms | ING
Selfservice nominal power | Settings |  | DSTO | SelfWRtg | ING
Selfservice nominal power factor | Settings |  | DSTO | SelfPFRtg | ING
Selfservice acceptable voltage range | Settings |  | DSTO | SelfVRngRtg | ING
Efficiency at rated capacity as percent | Settings |  | DSTO | EfcRtgPct | ASG
Rated Nominal frequency of usage of the DER | Settings |  | DSTO | HzNomRtg | ASG
Rated minimal frequency of usage of the DER | Settings |  | DSTO | HzMinRtg | ASG
Rated maximal frequency of usage of the DER | Settings |  | DSTO | HzMaxRtg | ASG
Internal identifier of the resource within a system which is using that resource. It complements the mRID defined as part of the EEname DO. Different DERIds may be defined for different system users. | Settings |  | DSTO | DERId | VSG

## DLOD
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of external (electrical, mechanical or communication) equipment to which the logical node is associated. | Descriptions |  | DLOD | EEName | DPL
Name plate of the logical node. | Descriptions |  | DLOD | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | DLOD | Beh | ENS | BehaviourModeKind
Reflects the state of the logical node related hardware and software. More detailed information related to the source of the problem may be provided by specific attribute of the logical node. | Status information |  | DLOD | Health | ENS | HealthKind
If true, the operation of the whole logical device has been switched (from remote) to local. | Status information |  | DLOD | LocKey | SPS
If true, the control behaviour is allowed at this level. | Status information |  | DLOD | Loc | SPS
Current state of operation of the distributed energy resource. | Status information |  | DLOD | DEROpSt | ENS | DERStateKind
State of external (electrical, mechanical or communication) equipment to which the logical node is associated. | Status information |  | DLOD | EEHealth | ENS | HealthKind
Operation time of the external (electrical, mechanical or communication) equipment since start of the operation. | Status information |  | DLOD | OpTmh | INS
The total amount of reactive power without impacting active power output if the distinction between absorbing and injecting reactive power is not significant (the use of this DO is mutually exclusive with the use of AvarTot and IvarTot) | Measured and metered values |  | DLOD | VArTot | MV
The total amount of reactive power available for absorbing even if possibly impacting active power output (the use of this DO is mutually exclusive with the use of VArTot) | Measured and metered values |  | DLOD | AvarTot | MV
The total amount of reactive power available for injecting even if possibly impacting active power output (the use of this DO is mutually exclusive with the use of VArTot) | Measured and metered values |  | DLOD | IvarTot | MV
The amount of reactive power available without impacting active power output if the distinction between absorbing and injecting reactive power is not significant (the use of this DO is mutually exclusive with the use of AvarAvl and IvarAvl) | Measured and metered values |  | DLOD | VArAvl | MV
The amount of reactive power available for absorbing without impacting active power output (the use of this DO is mutually exclusive with the use of VArAvl) | Measured and metered values |  | DLOD | AvarAvl | MV
The amount of reactive power available for injecting without impacting active power output (the use of this DO is mutually exclusive with the use of VArAvl) | Measured and metered values |  | DLOD | IvarAvl | MV
Actual self service energy used | Measured and metered values |  | DLOD | SelfSvcWh | MV
Actual percentage of apparent power output based on VAMax | Measured and metered values |  | DLOD | VAPct | MV
Available capability (measured or calculated) for increasing active output, including increasing generation of active power, even if currently consuming power. | Measured and metered values |  | DLOD | AvlUpW | MV
Available capability (measured or calculated) for decreasing active power, including increasing the consumption of active power, even if currently generating power. | Measured and metered values |  | DLOD | AvlDnW | MV
(controllable) Operating mode of the domain logical node that may be changed by operator. | Controls |  | DLOD | Mod | ENC | BehaviourModeKind
(controllable) If true, control authority is at station level and control from remote is disabled; otherwise control from remote is allowed. | Controls |  | DLOD | LocSta | SPC
(controllable) Operating with the value expressed in ctlVal (selected among the list specified in DERStateControlKind) initiates the appropriate transition request. The reading of its attribute stVal is meaningless. The resulting state of the DER shall be observed in the DEROpSt DO. | Controls |  | DLOD | DEROpStCtl | ENC | DERStateTransitionKind
Active power setpoint. Its mxVal attribute reflects the value of the setpoint that is requested. | Controls |  | DLOD | WSpt | APC
Reactive power setpoint. Its mxVal attribute reflects the value of the setpoint that is requested. | Controls |  | DLOD | VArSpt | APC
Active power setpoint (deprecated) | Controls |  | DLOD | OutWSet | ASG
Reactive power setpoint (deprecated) | Controls |  | DLOD | OutVarSet | ASG
(controllable) Operations count, can be reset to a value different than 0. | Controls |  | DLOD | OpCntRs | INC
Reference to the DER Unit LN which may be associated to this generic model LN | Settings |  | DLOD | DERUnit | ORG
Nameplate maximum Load active power rating at unity power factor | Settings |  | DLOD | WMaxRtg | ASG
Maximum voltage rating | Settings |  | DLOD | VMaxRtg | ASG
Minimum voltage rating | Settings |  | DLOD | VMinRtg | ASG
Maximum current rating under nominal voltage under nominal power factor while charging | Settings |  | DLOD | AMaxRtg | ASG
Nameplate maximum apparent charging power rating | Settings |  | DLOD | VAMaxRtg | ASG
Maximum nameplate charging ramp up rating | Settings |  | DLOD | WRpuMaxRtg | ASG
Maximum nameplate charging ramp down rating | Settings |  | DLOD | WRpdMaxRtg | ASG
Maximum nameplate charging ramp down rating | Settings |  | DLOD | WMax | ASG
Default ramp rate for changes in active power: percentage of WMax per second | Settings |  | DLOD | WRmp | ASG
Setting for maximum reactive power if the distinction between absorbing and injecting reactive power is not significant (the use of this DO is mutually exclusive with the use of AvarMax and IvarMax) | Settings |  | DLOD | VArMax | ASG
Setting for maximum absorbing reactive power (the use of this DO is mutually exclusive with the use of VArMax) | Settings |  | DLOD | AvarMax | ASG
Setting for maximum supply (injection) reactive power (the use of this DO is mutually exclusive with the use of VArMax) | Settings |  | DLOD | IvarMax | ASG
Setting for maximum voltage operational rating | Settings |  | DLOD | VMax | ASG
Setting for minimum voltage operational rating | Settings |  | DLOD | VMin | ASG
Setting for maximum operational current rating under nominal voltage under nominal power factor | Settings |  | DLOD | AMax | ASG
Setting for maximum apparent power while generating (the use of this DO is mutually exclusive with the use of AvaMax and IvaMax) | Settings |  | DLOD | VAMax | ASG
Setting for maximum absorbing apparent power (the use of this DO is mutually exclusive with the use of VAMax) | Settings |  | DLOD | AvaMax | ASG
Setting for maximum injecting apparent power (the use of this DO is mutually exclusive with the use of VAMax) | Settings |  | DLOD | IvaMax | ASG
Reference for reactive power setpoints. Selects which setpoint is active. | Settings |  | DLOD | VArSptRef | ENG | ReactivePowerRefParamKind
Reference to ECP directly connected at the output of the DER, the "plug" part. Note: The power management function ECP associated to this same resource will refer to the "socket" part. | Settings |  | DLOD | OutEcpRef | ORG
Connection type of ECP: connection to DER (Point of Connection (PoC)), to load, within Local Electric Power System (Local EPS), Point of Common Coupling (PCC), or directly to Area EPS | Settings |  | DLOD | EcpConnTyp | ENG | ECPConnKind
Phase type of electrical connection of the DER | Settings |  | DLOD | PhsConnTyp | ENG | PhaseKind
Type of DER | Settings |  | DLOD | DERTyp | ENG | DERUnitKind
Maximum temperature rating | Settings |  | DLOD | TmpMaxRtg | ASG
Exposure to fault rates as percent of ?? | Settings |  | DLOD | FltRtgPct | ASG
Max fault current rating | Settings |  | DLOD | FltAMaxRtg | ASG
Selfservice voltage | Settings |  | DLOD | SelfVRtg | ASG
Max fault duration rating | Settings |  | DLOD | FltDurMaxTms | ASG
Selfservice nominal power | Settings |  | DLOD | SelfWRtg | ASG
Selfservice nominal power factor | Settings |  | DLOD | SelfPFRtg | ASG
Selfservice acceptable voltage range | Settings |  | DLOD | SelfVRngRtg | ASG
Efficiency at rated capacity as percent | Settings |  | DLOD | EfcRtgPct | ASG
Rated Nominal frequency of usage of the DER | Settings |  | DLOD | HzNomRtg | ASG
Rated minimal frequency of usage of the DER | Settings |  | DLOD | HzMinRtg | ASG
Rated maximum frequency of usage of the DER | Settings |  | DLOD | HzMaxRtg | ASG
Internal identifier of the resource within a system which is using that resource. It complements the mRID defined as part of the EEname DO. Different DERIds may be defined for different system users. | Settings |  | DLOD | DERId | ASG

## DINV
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of external (electrical, mechanical or communication) equipment to which the logical node is associated. | Descriptions |  | DINV | EEName | DPL
Name plate of the logical node. | Descriptions |  | DINV | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | DINV | Beh | ENS | BehaviourModeKind
Reflects the state of the logical node related hardware and software. More detailed information related to the source of the problem may be provided by specific attribute of the logical node. | Status information |  | DINV | Health | ENS | HealthKind
If true, the operation of the whole logical device has been switched (from remote) to local. | Status information |  | DINV | LocKey | SPS
If true, the control behaviour is allowed at this level. | Status information |  | DINV | Loc | SPS
Alarm trigger status: Inverter detects loss of AC power | Status information |  | DINV | InvACLosAlm | SPS
Alarm trigger status: Inverter detects loss of DC power | Status information |  | DINV | InvDCLosAlm | SPS
Alarm trigger status: Inverter detects loss of grid power | Status information |  | DINV | InvGriLosAl | SPS
State of external (electrical, mechanical or communication) equipment to which the logical node is associated. | Status information |  | DINV | EEHealth | ENS | HealthKind
Operation time of the external (electrical, mechanical or communication) equipment since start of the operation. | Status information |  | DINV | OpTmh | INS
Active power setpoint of the inverter | Controls |  | DINV | WSpt | APC
Reactive power setpoint of the inverter | Controls |  | DINV | VArSpt | APC
Active power setpoint of the inverter (deprecated) | Controls |  | DINV | OutWSet | ASG
Reactive power setpoint of the inverter (deprecated) | Controls |  | DINV | OutVarSet | ASG
Inverter control source: current, voltage, voltagecurrent | Controls |  | DINV | InvCtlSrc | ENG | InverterControlSourceKind
(controllable) Operating mode of the domain logical node that may be changed by operator. | Controls |  | DINV | Mod | ENC | BehaviourModeKind
(controllable) If true, control authority is at station level and control from remote is disabled; otherwise control from remote is allowed. | Controls |  | DINV | LocSta | SPC
Rated active power of the inverter | Settings |  | DINV | WRtg | ASG
The continuous apparent power capability of the power inverter. | Settings |  | DINV | VARtg | ASG
PQV set of limiting curves. | Settings |  | DINV | WVArVLim | CSG
Active curve characteristic curve for PQV limit. | Settings |  | DINV | WVArVLimSet | CSG
Nominal frequency of switching. | Settings |  | DINV | SwHz | ASG
Type of cooling method: - Passive air cooling (heatsink) - Forced air cooling (fan + heatsink) - Fluid cooling (water) - Heat pipe | Settings |  | DINV | ClMthTyp | ENG | CoolingMethodKind
Type of isolation. | Settings |  | DINV | IsoTyp | ENG | IsolationKind
Type of AC system. | Settings |  | DINV | ACTyp | ENG | ACSystemKind
Maximum Input current limit. | Settings |  | DINV | InAMax | ASG
Maximum Input voltage limit. | Settings |  | DINV | InVMax | ASG
Rated bidirectional reactive power. | Settings |  | DINV | VArRtg | ASG
Rated voltage (intrinsic property) | Settings |  | DINV | VRtg | ASG

## DCCT
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of the logical node. | Descriptions |  | DCCT | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | DCCT | Beh | ENS | BehaviourModeKind
Reflects the state of the logical node related hardware and software. More detailed information related to the source of the problem may be provided by specific attribute of the logical node. | Status information |  | DCCT | Health | ENS | HealthKind
ISO 4217 currency 3-character code | Settings |  | DCCT | Ccy | CUG
Marginal operational cost per hour | Settings |  | DCCT | OpCost | ASG
Marginal operational cost per kWh | Settings |  | DCCT | OpWhCost | ASG
Cost to start up DER | Settings |  | DCCT | StrCost | ASG
Cost to stop DER | Settings |  | DCCT | StopCost | ASG
Cost to ramp DER per kW per minute | Settings |  | DCCT | RampCost | ASG
Incremental heat rate piecewise linear curve costs. | Settings |  | DCCT | HeatRteCost | CSG
Incremental carbon emission curve costs. | Settings |  | DCCT | CRteCost | CSG
(controllable) Operating mode of the domain logical node that may be changed by operator. | Controls |  | DCCT | Mod | ENC | BehaviourModeKind

## DCST
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of the logical node. | Descriptions |  | DCST | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | DCST | Beh | ENS | BehaviourModeKind
Reflects the state of the logical node related hardware and software. More detailed information related to the source of the problem may be provided by specific attribute of the logical node. | Status information |  | DCST | Health | ENS | HealthKind
ISO 4217 currency 3-character code | Settings |  | DCST | Ccy | CUG
Active curve characteristics for the incremental heat rate curve | Settings |  | DCST | HeatRteAct | CSG
Incremental heat rate piecewise linear curve costs. | Settings |  | DCST | HeatRteCost | CSG
Cost to start up DER | Settings |  | DCST | StrCost | ASG
Cost to stop DER | Settings |  | DCST | StopCost | ASG
Cost to ramp DER per kW per minute | Settings |  | DCST | RampCost | ASG
Incremental carbon emission curve costs. | Settings |  | DCST | CRteCost | CSG
(controllable) Operating mode of the domain logical node that may be changed by operator. | Controls |  | DCST | Mod | ENC | BehaviourModeKind

## MMET
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of the logical node. | Descriptions |  | MMET | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | MMET | Beh | ENS | BehaviourModeKind
Reflects the state of the logical node related hardware and software. More detailed information related to the source of the problem may be provided by specific attribute of the logical node. | Status information |  | MMET | Health | ENS | HealthKind
Plane of array insolation (insolation SIUnit [W/m2]). | Measured and metered values |  | MMET | PoaInsol | MV
Temperature of environment [°C]. | Measured and metered values |  | MMET | EnvTmp | MV
Wet bulb temperature (typically in °C). | Measured and metered values |  | MMET | WetBlbTmp | MV
Cloud cover level. | Measured and metered values |  | MMET | CloudCvr | MV
Humidity of environment (typically in %). | Measured and metered values |  | MMET | EnvHum | MV
Dew point. | Measured and metered values |  | MMET | DewPt | MV
Diffuse insolation (insolation SIUnit [W/m2]). | Measured and metered values |  | MMET | DffInsol | MV
Direct normal insolation (insolation SIUnit [W/m2]). | Measured and metered values |  | MMET | DctInsol | MV
Daylight duration (time elapsed between sunrise and sunset). | Measured and metered values |  | MMET | DlDur | MV
Total horizontal insolation (insolation SIUnit [W/m2]). | Measured and metered values |  | MMET | HorInsol | MV
Total horizontal wind direction. | Measured and metered values |  | MMET | HorWdDir | MV
Average horizontal wind speed. | Measured and metered values |  | MMET | HorWdSpd | MV
Vertical wind direction. | Measured and metered values |  | MMET | VerWdDir | MV
Average vertical wind speed. | Measured and metered values |  | MMET | VerWdSpd | MV
Maximum wind gust speed. | Measured and metered values |  | MMET | WdGustSpd | MV
Barometric pressure of environment. | Measured and metered values |  | MMET | EnvPres | MV
Rainfall (typically in mm – length SIUnit [m]). | Measured and metered values |  | MMET | RnFll | MV
Snowfall density (typically in g/cm3 – density SIUnit [kg/m3]). | Measured and metered values |  | MMET | SnwDen | MV
Snowfall temperature (typically in °C). | Measured and metered values |  | MMET | SnwTmp | MV
Snow cover (typically in mm – length SIUnit [m]). | Measured and metered values |  | MMET | SnwCvr | MV
Snowfall (typically in mm – length SIUnit [m]). | Measured and metered values |  | MMET | SnwFll | MV
Water equivalent of snowfall (typically in mm – length SIUnit [m]). | Measured and metered values |  | MMET | SnwEq | MV
(controllable) Operating mode of the domain logical node that may be changed by operator. | Controls |  | MMET | Mod | ENC | BehaviourModeKind

## MMXU
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of the logical node. | Descriptions |  | MMXU | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | MMXU | Beh | ENS | BehaviourModeKind
Reflects the state of the logical node related hardware and software. More detailed information related to the source of the problem may be provided by specific attribute of the logical node. | Status information |  | MMXU | Health | ENS | HealthKind
Indication of the current PF measurement quadrant. if set to true, then it is indicating overexcited quadrant, otherwise it is indicating the underexcited quadrant. This information needs to be considered in regards of the PF sign convention. | Status information |  | MMXU | PFExtQud | SPS
status of the power vector expressed through one of the 9 zones of the PQ diagram quadrant, based on the signing conventions set with PFSign and PFExt. | Status information |  | MMXU | PQSt | ENS | QuadrantRunningStateKind
Total real power in a three-phase circuit [W]. | Measured and metered values |  | MMXU | TotW | MV
Total reactive power in a three-phase circuit [VAr]. | Measured and metered values |  | MMXU | TotVAr | MV
The total apparent power in a three-phase circuit [VA]. | Measured and metered values |  | MMXU | TotVA | MV
Signed power factor in a three-phase circuit. The power factor is defined as ratio of the absolute active power to the apparent power (acc. IEV 131-11-46). Sign is added and determinded by the PF sign convention (DO PFSign). Calculation method of apparaent power is defined by the data object ClcTotVA. | Measured and metered values |  | MMXU | TotPF | MV
Frequency [Hz]. | Measured and metered values |  | MMXU | Hz | MV
Phase to phase voltages. | Measured and metered values |  | MMXU | PPV | DEL
Phase to neutral voltages. | Measured and metered values |  | MMXU | PNV | WYE
Phase to ground (line) voltages. | Measured and metered values |  | MMXU | PhV | WYE
Phase to ground/phase to neutral three phase currents. | Measured and metered values |  | MMXU | A | WYE
Phase to ground/phase to neutral real powers P. | Measured and metered values |  | MMXU | W | WYE
Phase to ground/phase to neutral reactive powers Q. | Measured and metered values |  | MMXU | VAr | WYE
Phase to ground/phase to neutral apparent powers S. | Measured and metered values |  | MMXU | VA | WYE
Phase to ground/phase to neutral signed power factors. The power factor is defined as the ratio of absolute active power to apparent power (acc.IEV 131-11-46). Sign is added and determined by the PF sign convention (DO PFSign). If current (I) and voltage (U) are sinusoidal and displaced by the angle phi, then the power factor is cos phi. Therefore, for the power factor per phase, value is contained in 'mag' and 'ang' is not used. | Measured and metered values |  | MMXU | PF | WYE
Phase to ground/phase to neutral impedances in a three-phase system. | Measured and metered values |  | MMXU | Z | WYE
Arithmetic average of the magnitude of current of the 3 phases: average(Ia,Ib,Ic). | Measured and metered values |  | MMXU | AvAPhs | MV
Arithmetic average of the magnitude of phase to phase voltage of the 3 phases: average(PPVa, PPVb, PPVc). | Measured and metered values |  | MMXU | AvPPVPhs | MV
Arithmetic average of the magnitude of phase to reference voltage of the 3 phases: average(PhVa, PhVb, PhVc). | Measured and metered values |  | MMXU | AvPhVPhs | MV
Arithmetic average of the magnitude of active power of the 3 phases: average(Wa, Wb, Wc). | Measured and metered values |  | MMXU | AvWPhs | MV
Arithmetic average of the magnitude of apparent power of the 3 phases: average(VAa, VAb, VAc). | Measured and metered values |  | MMXU | AvVAPhs | MV
Arithmetic average of the magnitude of reactive power of the 3 phases: average(VAra, VArb, VArc). | Measured and metered values |  | MMXU | AvVArPhs | MV
Arithmetic average of the magnitude of power factor of the 3 phases: average(PFa, PFb, PFc). | Measured and metered values |  | MMXU | AvPFPhs | MV
Arithmetic average of the magnitude of impedance of the 3 phases: average(Za, Zb, Zc). | Measured and metered values |  | MMXU | AvZPhs | MV
Maximum magnitude of current of the 3 phases: max(Ia,Ib,Ic). | Measured and metered values |  | MMXU | MaxAPhs | MV
Maximum magnitude of phase to phase voltage of the 3 phases: max(PPVa, PPVb, PPVc). | Measured and metered values |  | MMXU | MaxPPVPhs | MV
Maximum magnitude of phase to reference voltage of the 3 phases: max(PhVa, PhVb, PhVc). | Measured and metered values |  | MMXU | MaxPhVPhs | MV
Maximum magnitude of active power of the 3 phases: max(Wa, Wb, Wc). | Measured and metered values |  | MMXU | MaxWPhs | MV
Maximum magnitude of apparent power of the 3 phases: max(VAa, VAb, VAc). | Measured and metered values |  | MMXU | MaxVAPhs | MV
Maximum magnitude of reactive power of the 3 phases: max(VAra, VArb, VArc). | Measured and metered values |  | MMXU | MaxVArPhs | MV
Maximum magnitude of power factor of the 3 phases: max(PFa, PFb, PFc). | Measured and metered values |  | MMXU | MaxPFPhs | MV
Maximum magnitude of impedance of the 3 phases: max(Za, Zb, Zc). | Measured and metered values |  | MMXU | MaxZPhs | MV
Minimum magnitude of current of the 3 phases: min(Ia,Ib,Ic). | Measured and metered values |  | MMXU | MinAPhs | MV
Minimum magnitude of phase to phase voltage of the 3 phases: min(PPVa, PPVb, PPVc). | Measured and metered values |  | MMXU | MinPPVPhs | MV
Minimum magnitude of phase to reference voltage of the 3 phases: min(PhVa, PhVb, PhVc). | Measured and metered values |  | MMXU | MinPhVPhs | MV
Minimum magnitude of active power of the 3 phases: min(Wa, Wb, Wc). | Measured and metered values |  | MMXU | MinWPhs | MV
Minimum magnitude of apparent power of the 3 phases: min(VAa, VAb, VAc). | Measured and metered values |  | MMXU | MinVAPhs | MV
Minimum magnitude of reactive power of the 3 phases: min(VAra, VArb, VArc). | Measured and metered values |  | MMXU | MinVArPhs | MV
Minimum magnitude of power factor of the 3 phases: min(PFa, PFb, PFc). | Measured and metered values |  | MMXU | MinPFPhs | MV
Minimum magnitude of impedance of the 3 phases: min(Za, Zb, Zc). | Measured and metered values |  | MMXU | MinZPhs | MV
Rate of change of frequency [Hz/s]. | Measured and metered values |  | MMXU | HzRte | MV
(controllable) Operating mode of the domain logical node that may be changed by operator. | Controls |  | MMXU | Mod | ENC | BehaviourModeKind

## MMTR
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of the logical node | Descriptions |  | MMTR | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | MMTR | Beh | ENS | BehaviourModeKind
Reflects the state of the logical node related hardware and software. More detailed information related to the source of the problem may be provided by specific attribute of the logical node. | Status information |  | MMTR | Health | ENS | HealthKind
Net apparent energy since last reset. | Status information |  | MMTR | TotVAh | BCR
Net real energy since last reset. | Status information |  | MMTR | TotWh | BCR
Net reactive energy since last reset. | Status information |  | MMTR | TotVArh | BCR
Real energy supply (default direction: towards busbar). | Status information |  | MMTR | SupWh | BCR
Reactive energy supply (default direction: towards busbar). | Status information |  | MMTR | SupVArh | BCR
Real energy demand (direction: from busbar). | Status information |  | MMTR | DmdWh | BCR
Reactive energy demand (direction: from busbar). | Status information |  | MMTR | DmdVArh | BCR
(controllable) Operating mode of the domain logical node that may be changed by operator. | Controls |  | MMTR | Mod | ENC | BehaviourModeKind

## FSCC
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of the logical node | Descriptions |  | FSCC | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | FSCC | Beh | ENS | BehaviourModeKind
Reflects the state of the logical node related hardware and software. More detailed information related to the source of the problem may be provided by specific attribute of the logical node. | Status information |  | FSCC | Health | ENS | HealthKind
Indication of which schedule is active as an object reference. As long as no schedule is active the quality of the value is invalid. The active schedule is selected by the schedule controller within the running schedules based on the priority of the running schedules. | Status information |  | FSCC | ActSchdRef | ORS
Current value determined by the scheduling system. As long as no schedule is active the quality of the value is invalid. The unit of this data shall be the same as the unit of the data object(s) FSCH.ValING. | Status information |  | FSCC | ValINS | INS
Current value determined by the scheduling system. As long as no schedule is active the quality of the value is invalid. | Status information |  | FSCC | ValSPS | SPS
Current value determined by the scheduling system. As long as no schedule is active the quality of the value is invalid. | Status information |  | FSCC | ValENS | ENS | EnumDA
Current value determined by the schedule. As long as the schedule is not running the quality of the value shall be set to invalid. The unit of this data shall be the same as the unit of the data object(s) FSCH.ValASG. | Measured and metered values |  | FSCC | ValMV | MV
Object reference to the entity controlled by the schedule. | Settings |  | FSCC | CtlEnt | ORG
Object reference of schedule n (an LN reference to the LN of class FSCH). | Settings |  | FSCC | Schd | ORG
Object reference of data object bound to the input n. | Settings |  | FSCC | InRef | ORG
(controllable) Operating mode of the domain logical node that may be changed by operator. | Controls |  | FSCC | Mod | ENC | BehaviourModeKind

## FSCH
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of the logical node | Descriptions |  | FSCH | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | FSCH | Beh | ENS | BehaviourModeKind
Reflects the state of the logical node related hardware and software. More detailed information related to the source of the problem may be provided by specific attribute of the logical node. | Status information |  | FSCH | Health | ENS | HealthKind
State of this schedule | Status information |  | FSCH | SchdSt | ENS | ScheduleStateKind
The current schedule entry of a running schedule. This is the Data-Instance-ID of the data object ValXXX (e.g. ValASG). As long as the schedule is not running the value shall be 0. | Status information |  | FSCH | SchdEntr | INS
Current value determined by the schedule. As long as the schedule is not running the quality of the value is invalid. The unit of this data shall be the same as the unit of the data object(s) ValING. | Status information |  | FSCH | ValINS | INS
Current value determined by the schedule. As long as the schedule is not running the quality of the value is invalid. | Status information |  | FSCH | ValSPS | SPS
Current value determined by the schedule. As long as the schedule is not running the quality of the value is invalid. | Status information |  | FSCH | ValENS | ENS | EnumDA
The time when the schedule started running. If the schedule is not running, the quality of the value is set to invalid. | Status information |  | FSCH | ActStrTm | TCS
The next time when the schedule is planned/intented to start or re-start running. If no schedules are planned running, the quality of the value is set to invalid. | Status information |  | FSCH | NxtStrTm | TCS
Enumeration reflecting the potential error which has happened at the latest Schedule Enabling request | Status information |  | FSCH | SchdEnaErr | ENS | ScheduleEnablingErrorKind
Current value determined by the schedule. As long as the schedule is not running the quality of the value is invalid. The unit of this data shall be the same as the unit of the data object(s) ValASG | Measured and metered values |  | FSCH | ValMV | MV
(controllable) Operating with value true initiates enable transition request according to the state diagram; operating with value false is ignored. The change of its status value is a local issue. | Controls |  | FSCH | EnaReq | SPC
(controllable) Operating with value true initiates disable transition request according to the state diagram; operating with value false is ignored. The change of its status value is a local issue. | Controls |  | FSCH | DsaReq | SPC
The priority relation of this schedule (0..n) with higher numbers superseding lower numbers. Shall be a positive value. If missing the default is zero. | Settings |  | FSCH | SchdPrio | ING
The number of schedule entries that are valid out of the instantiated ValASG, ValING, ValSPG or ValENG. NumEntr shall be > 0. NumEntr is <= number of instantiated Val[ASG¦ING¦SPG¦ENG]'s | Settings |  | FSCH | NumEntr | ING
The schedule interval duration in time entities as specified in the unit. The SIUnit is mandatory in this data object. The total duration of a schedule shall be (NumEntr x SchdIntv). | Settings |  | FSCH | SchdIntv | ING
The ASG scheduled values (current value output as MV). | Settings |  | FSCH | ValASG | ASG
The ING scheduled values (current value output as INS). | Settings |  | FSCH | ValING | ING
The SPG scheduled values (current value as SPS). | Settings |  | FSCH | ValSPG | SPG
The ENG scheduled values (current value as ENS). | Settings |  | FSCH | ValENG | ENG | EnumDA
Start time of the schedule in UTC time. | Settings |  | FSCH | StrTm | TSG
If true, the change of the schedule to the running and activated state is triggered by an external event and not by the start time. The external event is referenced through 'InSyn'. | Settings |  | FSCH | EvtTrg | SPG
Object reference of the external trigger if the schedule is triggered by an event. | Settings |  | FSCH | InSyn | ORG
If true, once terminated or disabled, the schedule will change to the validated state, otherwise it will change to the not ready state. | Settings |  | FSCH | SchdReuse | SPG
Object reference of data object bound to the input n. | Settings |  | FSCH | InRef | ORG
(controllable) Operating mode of the domain logical node that may be changed by operator. | Controls |  | FSCH | Mod | ENC | BehaviourModeKind

## DECP
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of the logical node | Descriptions |  | DECP | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | DECP | Beh | ENS | BehaviourModeKind
Reflects the state of the logical node related hardware and software. More detailed information related to the source of the problem may be provided by specific attribute of the logical node. | Status information |  | DECP | Health | ENS | HealthKind
Type of circuit phases | Settings |  | DECP | PhsConnTyp | ENS | PhaseKind
Default reference voltage for functions using voltage at this ECP as input | Settings |  | DECP | VRef | ASG
Percent of VRef to use in calculating the voltage to use in operational function calculations | Settings |  | DECP | VRefPct | ASG
Electrical active power rating at ECP | Settings |  | DECP | WRtg | ASG
Reactive power rating at ECP | Settings |  | DECP | VArRtg | ASG
Apparent power rating at ECP | Settings |  | DECP | VARtg | ASG
Voltage rating at ECP | Settings |  | DECP | VRtg | ASG
Nominal frequency at ECP | Settings |  | DECP | HzNom | ASG
Rated maximum voltage | Settings |  | DECP | VMax | ASG
Rated minimum voltage | Settings |  | DECP | VMin | ASG
Identity of electrical reference point as a Visible String | Settings |  | DECP | ElcRefId | VSG
Indication whether the active power from the DER referencing this ECP is included in the measurements coming from the ECP. This is important for managing Generation and Load Following, as well as Peak Power Limiting functions. | Settings |  | DECP | DERMsIncl | SPG
Reference to electrical measurement/calculation function, typically MMXU, MMXN or MMDC, MMTR LN instances | Settings |  | DECP | ElcMsRef | ORG
(controllable) Operating mode of the domain logical node that may be changed by operator. | Controls |  | DECP | Mod | ENC | BehaviourModeKind

## DPCC
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of the logical node | Descriptions |  | DPCC | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | DPCC | Beh | ENS | BehaviourModeKind
Reflects the state of the logical node related hardware and software. More detailed information related to the source of the problem may be provided by specific attribute of the logical node. | Status information |  | DPCC | Health | ENS | HealthKind
(controllable) Operating mode of the domain logical node that may be changed by operator. | Controls |  | DPCC | Mod | ENC | BehaviourModeKind
Identification of the ECP from the Area Electric Power System | Settings |  | DPCC | AreaEpsEcpId | VSG
Maximum active power at the PCC for area EPS | Settings |  | DPCC | AreaEpsWMax | ASG
Type of circuit phases | Settings |  | DPCC | PhsConnTyp | ENS | PhaseKind
Default reference voltage for functions using voltage at this ECP as input. It may be overridden by Vref setpoints in specific operational functions. | Settings |  | DPCC | VRef | ASG
Percent of VRef to use in calculating the voltage to use in operational function calculations | Settings |  | DPCC | VRefPct | ASG
Electrical active power rating at ECP | Settings |  | DPCC | WRtg | ASG
Reactive power rating at ECP | Settings |  | DPCC | VArRtg | ASG
Apparent power rating at ECP | Settings |  | DPCC | VARtg | ASG
Voltage rating at ECP | Settings |  | DPCC | VRtg | ASG
Nominal frequency at ECP | Settings |  | DPCC | HzNom | ASG
Rated maximum voltage | Settings |  | DPCC | VMax | ASG
Rated minimum voltage | Settings |  | DPCC | VMin | ASG
Identity of electrical reference point as a Visible String | Settings |  | DPCC | ElcRefId | VSG
Indication whether the active power from the DER referencing this ECP is included in the measurements coming from the ECP. This is important for managing Generation and Load Following, as well as Peak Power Limiting functions. | Settings |  | DPCC | DERMsIncl | SPG
Reference to electrical measurement/calculation function, typically MMXU, MMXN or MMDC, MMTR LN instances | Settings |  | DPCC | ElcMsRef | ORG

## DVER
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of the logical node | Descriptions |  | DVER | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | DVER | Beh | ENS | BehaviourModeKind
Reflects the state of the logical node related hardware and software. More detailed information related to the source of the problem may be provided by specific attribute of the logical node. | Status information |  | DVER | Health | ENS | HealthKind
(controllable) Operating mode of the domain logical node that may be changed by operator. | Controls |  | DVER | Mod | ENC | BehaviourModeKind
Reference to included electrical reference points which could be real or virtual | Settings |  | DVER | InclElcRef | ORG
Identity of electrical reference point as a Visible String | Settings |  | DVER | ElcRefId | VSG
Reference to electrical measurement/calculation function, typically MMXU, MMXN or MMDC, MMTR LN instances | Settings |  | DVER | ElcMsRef | ORG

## DPMC
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of the logical node | Descriptions |  | DPMC | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | DPMC | Beh | ENS | BehaviourModeKind
Reflects the state of the logical node related hardware and software. More detailed information related to the source of the problem may be provided by specific attribute of the logical node. | Status information |  | DPMC | Health | ENS | HealthKind
Current top priority operational function driving the setting of the expected active power of the concerned DER. | Status information |  | DPMC | WTopFct | ORS
Current top priority operational function driving the setting of the expected reactive power of the concerned DER. | Status information |  | DPMC | VArTopFct | ORS
If true, the operation of the whole logical device has been switched (from remote) to local. | Status information |  | DPMC | LocKey | SPS
If true, the control behaviour is allowed at this level. | Status information |  | DPMC | Loc | SPS
(controllable) Operating mode of the domain logical node that may be changed by operator. | Controls |  | DPMC | Mod | ENC | BehaviourModeKind
(controllable) If true, control authority is at station level and control from remote is disabled; otherwise control from remote is allowed. | Controls |  | DPMC | LocSta | SPC
Total active power requested to the (DER) resource associated to this power management function. This resource may be hierarchically composed of many DERs. | Measured and metered values |  | DPMC | ReqTotW | MV
Minimum total active power requested to the (DER) resource associated to this power management function. This resource may be hierarchically composed of many DERs. | Measured and metered values |  | DPMC | ReqTotWMin | MV
Maximum total active power requested to the (DER) resource associated to this power management function. This resource may be hierarchically composed of many DERs. | Measured and metered values |  | DPMC | ReqTotWMax | MV
Active power setpoint. Its mxVal attribute reflects the value of the setpoint that is requested. | Controls |  | DPMC | WSpt | APC
Active power setpoint (deprecated) | Controls |  | DPMC | OutWSet | ASG
Minimum limiting setpoint of the DER's active power. Its mxVal attribute reflects the value of the setpoint that is requested. | Controls |  | DPMC | WMinSpt | APC
Limiting setpoint of the DER's active power. Ist mxVal attribute reflects the value of the setpoint that is requested. | Controls |  | DPMC | WMaxSpt | APC

## LPHD
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of the logical device | Descriptions |  | LPHD | NamPlt | LPL
Name plate of external (electrical, mechanical or communication) equipment to which the logical node is associated. | Descriptions |  | LPHD | PhyNam | DPL
Reflects the state of the physical device related hardware and software. | Status information |  | LPHD | PhyHealth | ENS | HealthKind
If true, the physical device is a proxy (i.e., the logical device embedding this logical node is representing another physical device). | Status information |  | LPHD | Proxy | SPS

## LLN0
Explanation | Type | Prefix | IEC 61850 LN | IEC 61850 DO | CDC | EnumKind | IEC 61850 DA | FC | Source
Name plate of the logical device | Descriptions |  | LLN0 | NamPlt | LPL
Read-only value, describing the behaviour of the logical device. For a root logical device, it is the same as the mode ('LLN0.Mod'). For non-root logical device, it depends on its own current operating mode ('LLN0.Mod'), and the current operating behaviour of the logical device that contains it (containing 'LLN0.Beh'). | Status information |  | LLN0 | Beh | ENS | BehaviourModeKind
Reflects the state of the logical device related hardware and software. It is derived from the worst (most critical) value of the health attribute of all the domain logical nodes contained in the logical device: 'Health' = max('DomainLN[i].Health'). | Status information |  | LLN0 | Health | ENS | HealthKind
If true, the operation of the whole logical device has been switched (from remote) to local. | Status information |  | LLN0 | LocKey | SPS
If true, the control behaviour is allowed at this level. | Status information |  | LLN0 | Loc | SPS
(controllable) Operating mode of the logical device that may be changed by operator; its value influences behaviour of the domain logical nodes ('DomainLN.Beh') contained in the logical device. | Controls |  | LLN0 | Mod | ENC | BehaviourModeKind
(controllable) If true, control authority is at station level and control from remote is disabled; otherwise control from remote is allowed. | Controls |  | LLN0 | LocSta | SPC
If true, authority control from multiple levels is allowed, otherwise no other control level is allowed. | Controls |  | LLN0 | MltLev | SPG