## Introduction
Coordination for preparation of the comprehensive PV communication data model
User group of this document:
This file is supposed to be used within the Serendi PV consortium for the implementation in task T6.3, subtask 6.3.2; Please read this short introduction carefully before starting to work with other sheets
Main objective of this subtask:
collecting as many parameters as possible for the registration, operation, monitoring and control of PV inverter, and map those parameters to standard protocol(s); THU focus on the implementation of an IEC 61850 based automation framework
Structure of this document
The file consists fo following parts:
- Parameter_Collection: this is the main sheet for the collaboration, here we will document the essential parameters based on literature research/working experience/technical specification/etc..These parameter will provide comprehensive information that covers various application areas.
- Lists of Values: the lists of avaiable values necessary/available for the parameter collection, inputs from partners are welcome at anytime, xy are place holder for new options
- IEC 61850 short description: a short description of the IEC 61850 standard series and previous implementation of the THU
- IEC 61850 LNs: summary of the IEC 61850 Logical Nodes involved in the comprehensive PV communication data model
- Mappting to IEC 61850: this sheet will be filled by THU, it contains essential information about the parameter mapping to IEC 61850 regarding the implementation in the software application.
- table xy
* Add your table as a new sheet if any mapping to other standard protocols is considered (e.g. DNP3, IEC-60870-5-104)
Sections in the sheet "Parameter_Collection"
- Data object: detailed information of the parameters, explanation for the headers and available values can be found in the sheet "Lists of values"
- Editor information: information about associated project partners (who would like to add it to the list, why is the parameter necessary)
- Interoperability: the interoperability regarding other standard/proprieitary protocols (is it supported in that protocol?)
- Parameter application: how would the parameters be used in the future (which partner is going to use it, and to which Serendi PV tast is it linked)
Some hints for editing the sheet "Parameter_Collection"
- please only add new parameters to the list, don't change the information of existing parameters in section "Data object" and "Editor Information"
- if an existing parameter proposed by other partners can also be useful for you, then just tick the column of your organization in the section "Parameter Application/ user"
- if an existing parameter proposed by other partners can also be useful for you, but you suggest different data format/transmission rate/category etc., then you should add a new row with your parameter
- to define the interlink with other tasks, tick the columns in the section "Parameter Application/ interlink with other working packages", if the application of one parameter in other WP/tasks is clearly identified
- highlight the cell with yellow background color or add comments if there is anything to be clarified
- any comment about the layout and structure is welcome
Breakdown description of the columns in the sheet "Parameter_Collection"
Data Objects - Category: category of the information, values should be taken from the list in sheet "Lists of Values"; the values are not given by any standard, just a proposal of THU, you can add more to the list
Data Objects - Object: this column defines to which object the charateristics described by this parameter belongs, values should be taken from the list in sheet "Lists of Values"
Data Objects - Name (if exists): if one parameter comes from a specific protocol/standard, you can also leave its name here in this column
Data Objects - description: a short description of the parameter, values should be defined by the editor
Data Objects - type: type of the parameter, values should be taken from the list in sheet "Lists of Values"
Data Objects - unit: unit of the parameter, values should be defined by the editor
Data Objects - R/W: read/write permission of the parameter, values should be taken from the list in sheet "Lists of Values"
Data Objects - transmission: transmission frequency of the parameter, values should be taken from the list in sheet "Lists of Values"
Editor Information - origin: the origin/source of the parameter, values should be taken from the list in sheet "Lists of Values"
Editor Information - contributor: partner that adds this parameter to the list, values should be taken from the list in sheet "Lists of Values"
Interoperability - interoperability (inverter side): the interoperability of the parameter regarding different field-bus standards, please put a x or the name of the parameter in the column, when it is given by that standard
Interoperability - interoperability (DSO side): the interoperability of the parameter regarding different tele-communication standards, please put a x or the name of the parameter in the column, when it is given by that standard
Parameter application - user: this column indicates the potential user (within the consortium) of that parameter, please put a x in the column, when that parameter will probably used by your organization
Parameter application - interlink with other working packages: only optional, please put a x in the column, when this parameter could be useful in other tasks

## Note for IEC61850 mapping
Some important notes
we leave out the inlanding parameters, calculation relevant settings and test settings
no calculation and data transfer inside the data model
Beh, Mod, Health not specified, we don't play around with these settings. These nodes will be automatically created during model generation, as they are mandatory nodes, but they will not be listed in the matching table.
no use of mixed DER, if it is the case, consider them separately
emergency mode is not considered
Autorization and authentification provided by Smart-Meter-Infrastructure
All controllable resources are fully controllable
DER completely shut down will not be an option in our case, instead use Wmax and other settings to limit the active/reactive power. -> we do not actively connect or disconnect the DER to/from the grid
Over-/underexciting ratings and settings are not considered
switching between interconnected and not interconnected to the grid is not considered, assume that the DER is always interconnected
No autonomous operational functions -> we always assume that Mod.stVal = 1 (On), and Beh in LN also stays at 1
possibly reduce the usage of ORG and other reference parameters for simplicity
virtual power plant, aggregation is not yet considered (the LN DVER is not in use)
not strictly refering to the presece condition defined in IEC-61850
most of the DA in LN DINV could be replaced by the same ones in LN DGEN

## Parameter_Collection
Data objects | [7 empty] | Mapping to IEC 61850 | [7 empty] | Editor information |  | Interoperability | [7 empty] | Parameter application
Category | Object | Name (if exists) | description | type | unit | R/W | transmission | LD | Prefix | LN | DO | CDC | DA | FC | EnumKInd | origin | contributor | interoperability (inverter side) |  |  |  | interoperability (DSO side) |  |  |  | user | [5 empty] | interlink with other working packages
[9 empty] | Prefix | LN | DO | CDC | DA | FC |  |  |  | SunSpec | Modbus | REST-API | others | IEC 61850 | DNP3 | IEC 60870-5-104 | others | THU | FIB | ING | MLS | SGIS | BI | T6.1 | T6.2 | T6.3 | T6.4 | T6.5 | T6.6 | WP5 | WP7 | WP8
OWNER_INFO | Owner |  | Prosumer UUID | character | / | R | Initial | OWNER | Prosumer_ | LPHD | PhyNam | DPL | name |  |  | others | FIB |  |  | x
OWNER_INFO | Owner |  | responsible DSO | character | / | R | change | OWNER | Prosumer_ | LPHD | PhyNam | DPL | primeOper |  |  | registry | THU
OWNER_INFO | Owner |  | responsible MPO | character | / | R | change | OWNER | Prosumer_ | LPHD | PhyNam | DPL | secondOper |  |  | registry | THU
OWNER_INFO | Owner |  | postal code | character | / | R | Initial | OWNER | Prosumer_ | LPHD | PhyNam | DPL |  |  |  | registry | THU
GEO_REF | Owner |  | Prosumer Label | character | / | R | Initial | OWNER | Prosumer_ | LPHD | PhyNam | DPL | ePSName |  |  | registry | FIB
GEO_REF | Owner |  | location | character | / | R | Initial | OWNER | Prosumer_ | LPHD | PhyNam | DPL | location |  |  | others | FIB |  |  | x
GEO_REF | Owner |  | geo longtitude | float | / | R | Initial | OWNER | Prosumer_ | LPHD | PhyNam | DPL | longitude |  |  | registry | THU
GEO_REF | Owner |  | geo latitude | float | / | R | Initial | OWNER | Prosumer_ | LPHD | PhyNam | DPL | latitude |  |  | registry | THU
MKT_IF | Owner |  | list of market partners | character | / | R | change | OWNER | Prosumer_ | LPHD | PhyNam | DPL | d |  |  | experience | THU
MKT_IF | Owner |  | metering number | character | / | R | change | OWNER | Prosumer_ | LPHD | PhyNam | DPL | mRID |  |  | experience | THU
HW_META | Communication Unit |  | CLS-gateway name | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | name | DC |  | IEC 61853 | THU
HW_META | Communication Unit |  | CLS-gateway hardware vendor | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | vendor | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | Communication Unit |  | CLS-gateway hardware model | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | model | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | Communication Unit |  | CLS-gateway hardware serial number | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | serNum | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
SW_META | Communication Unit |  | CLS-gateway software revision | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | swRev | DC |  | thucls | THU |  |  |  |  | x
HW_META | Communication Unit |  | CLS-gateway location | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | location | DC |  | IEC 61850 | THU
HW_META | Communication Unit |  | CLS-gateway longitude, WGS84 coordinates | float | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | longitude | DC |  | IEC 61850 | THU
HW_META | Communication Unit |  | CLS-gateway latitude, WGS84 coordinates | float | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | latitude | DC |  | IEC 61850 | THU
HW_META | Communication Unit |  | CLS-gateway altitude | float | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | altitude | DC |  | IEC 61850 | THU
HW_META | Communication Unit |  | CLS-gateway owner | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | owner | DC |  | IEC 61850 | THU
HW_META | Communication Unit |  | CLS-gateway connected electrical power system | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | ePSName | DC |  | IEC 61850 | THU
HW_META | Communication Unit |  | CLS-gateway primary operator | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | primeOper | DC |  | IEC 61850 | THU
HW_META | Communication Unit |  | CLS-gateway secondary operator | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | secondOper | DC |  | IEC 61850 | THU
STAT_INFO | Communication Unit |  | CLS-gateway hardware reversion | character | / | R | Change | CLS | Hardware_ | LPHD | PhyNam | DPL | hwRev | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
STAT_INFO | Communication Unit |  | CLS-gateway hardware UUID | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | mRID | DC |  | IEC 61850 | THU |  |  |  |  | x |  |  |  | x
STAT_INFO | Communication Unit |  | CLS-gateway hardware description | character | / | R | change | CLS | Hardware_ | LPHD | PhyNam | DPL | d | DC |  | IEC 61850 | THU |  |  |  |  | x |  |  |  | x
STAT_INFO | Communication Unit |  | CLS-gateway hardware failure description | character | / | R | Change | CLS | Hardware_ | LPHD | Beh | ENS | d | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
STAT_INFO | Communication Unit |  | CLS-application platform name | character | / | R | Initial | CLS | Platform_ | LPHD | PhyNam | DPL | name | DC |  | IEC 61853 | THU
STAT_INFO | Communication Unit |  | CLS-application platform vendor | character | / | R | Initial | CLS | Platform_ | LPHD | PhyNam | DPL | vendor | DC |  | thucls | THU
STAT_INFO | Communication Unit |  | CLS-application platform software revision | character | / | R | Initial | CLS | Platform_ | LPHD | PhyNam | DPL | swRev | DC |  | thucls | THU
STAT_INFO | Communication Unit |  | CLS-application platform hardware reversion | character | / | R | Change | CLS | Platform_ | LPHD | PhyNam | DPL | hwRev | DC |  | thucls | THU
STAT_INFO | Communication Unit |  | CLS-application platform failure description | character | / | R | Change | CLS | Platform_ | LPHD | Beh | ENS | d | DC |  | thucls | THU
SW_META | Communication Unit |  | CLS-software plug-in application provider | character | / | R | Initial | CLS |  | LLN0 | NamPlt | LPL | vendor | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
SW_META | Communication Unit |  | CLS-software application version | character | / | R | Initial | CLS |  | LLN0 | NamPlt | LPL | swRev | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
SW_META | Communication Unit |  | CLS-software application description | character | / | R | Initial | CLS |  | LLN0 | NamPlt | LPL | d | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
SW_META | Communication Unit |  | A placeholder for later use | character | / | R | Initial | CLS |  | LLN0 | NamPlt | LPL | configRev | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
STAT_INFO | Communication Unit |  | CLS-software failure description | character | / | R | Change | CLS |  | LLN0 | Beh | ENS | d | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
OP_FUNC | Communication Unit |  | local controller lock | boolean | / | R | Change | CLS | [7 empty] | thucls | THU |  |  |  |  | x |  |  |  | x
STAT_INFO | Communication Unit |  | CLS connectivity (defined by the IEC61850 client) | float | % | R/W | Change | CLS | [7 empty] | experience | THU
SW_META | PCC |  | Name plate of the logical node | character | / | R | Initial | PCC |  | LLN0 | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
SW_META | PCC |  | Name plate of the logical node | character | / | R | Initial | PCC |  | LLN0 | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
SW_META | PCC |  | Number of PV Inverters (represent integer by string) | character | / | R | Initial | PCC |  | LLN0 | NamPlt | LPL | d | DC |  | others | SGIS
SW_META | PCC |  | A placeholder for later use | character | / | R | Initial | PCC |  | LLN0 | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
STAT_INFO | PCC |  | PCC data service failure description | character | / | R | Change | PCC |  | LLN0 | Beh | ENS | d | DC |  | IEC 61850 | THU
HW_META | PCC |  | PCC service provider | character | / | R | Initial | PCC |  | DPCC | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
HW_META | PCC |  | PCC service software version | character | / | R | Initial | PCC |  | DPCC | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
HW_META | PCC |  | PCC service description | character | / | R | Initial | PCC |  | DPCC | NamPlt | LPL | d | DC |  | IEC 61850 | THU
HW_META | PCC |  | A placeholder for later use | character | / | R | Initial | PCC |  | DPCC | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
CTRL_PARA | PCC |  | Identification of the ECP from the Area Electric Power System | character | / | R | Initial | PCC |  | DPCC | AreaEpsEcpId | VSG | setVal | SP |  | IEC 61850 | THU
CTRL_PARA | PCC |  | Maximum active power at the PCC for area EPS | float | W | R | Initial | PCC |  | DPCC | AreaEpsWMax | ASG | setMag | SP |  | IEC 61850 | THU |  |  |  |  | x |  |  |  | x
HW_META | PCC |  | Type of circuit phases | enumeration | / | R | Initial | PCC |  | DPCC | PhsConnTyp | ENS | stVal | ST | PhaseKind | IEC 61850 | THU
SETTING | PCC |  | Default reference voltage for functions using voltage at this ECP as input. It may be overridden by Vref setpoints in specific operational functions. | float | V | R/W | change | PCC |  | DPCC | VRef | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PCC |  | Percent of VRef to use in calculating the voltage to use in operational function calculations | float | % | R/W | change | PCC |  | DPCC | VRefPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PCC |  | Electrical active power rating at ECP | float | W | R/W | change | PCC |  | DPCC | WRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PCC |  | Reactive power rating at ECP | float | Var | R/W | change | PCC |  | DPCC | VArRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PCC |  | Apparent power rating at ECP | float | VA | R/W | change | PCC |  | DPCC | VARtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PCC |  | Voltage rating at ECP | float | V | R/W | change | PCC |  | DPCC | VRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PCC |  | Nominal frequency at ECP | float | Hz | R/W | change | PCC |  | DPCC | HzNom | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PCC |  | Rated maximum voltage | float | V | R/W | change | PCC |  | DPCC | VMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PCC |  | Rated minimum voltage | float | V | R/W | change | PCC |  | DPCC | Vmin | ASG | setMag | SP |  | IEC 61850 | THU
CTRL_PARA | PCC |  | Identity of electrical reference point as a Visible String | character | / | R/W | change | PCC |  | DPCC | ElcRefId | VSG | setVal | SP |  | IEC 61850 | THU
CTRL_PARA | PCC |  | Determine self-consumption; Indication whether the active power from the DER referencing this ECP is included in the measurements coming from the ECP. This is important for managing Generation and Load Following, as well as Peak Power Limiting functions. | boolean | / | R | change | PCC |  | DPCC | DERMsIncl | SPG | setVal | SP |  | IEC 61850 | THU
HW_META | PCC |  | measuring unit vendor | character | / | R | Initial | PCC |  | MMXU | NamPlt | LPL | vendor | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | PCC |  | measuring unit software version | character | / | R | Initial | PCC |  | MMXU | NamPlt | LPL | swRev | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | PCC |  | measuring unit description | character | / | R | Initial | PCC |  | MMXU | NamPlt | LPL | d | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | PCC |  | A placeholder for later use | character | / | R | Initial | PCC |  | MMXU | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
STAT_INFO | PCC |  | status of the power vector expressed through one of the 9 zones of the PQ diagram quadrant, based on the signing conventions set with PFSign and PFExt. | enumeration | / | R | change | PCC |  | MMXU | PQSt | ENS | stVal | ST | QuadrantRunningStateKind | IEC 61850 | THU
MEAS_VAL | PCC |  | total active power measurement | float | W | R | change & integrity | PCC |  | MMXU | TotW | MV | mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | PCC |  | total reactive power measurement | float | Var | R | change & integrity | PCC |  | MMXU | TotVar | MV | mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | PCC |  | total apparent power measurement | float | VA | R | change & integrity | PCC |  | MMXU | TotVA | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | ratio of the absolute active power to the apparent power | float | / | R | change & integrity | PCC |  | MMXU | TotPF | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | frequency | float | Hz | R | change & integrity | PCC |  | MMXU | Hz | MV | mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | PCC |  | Phase to phase voltages. | float | V | R | change & integrity | PCC |  | MMXU | PPV | DEL | phsAB/BC/CA.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Phase to neutral voltages. | float | V | R | change & integrity | PCC |  | MMXU | PNV | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Phase to ground (line) voltages. | float | V | R | change & integrity | PCC |  | MMXU | PhV | WYE | phsA/B/C.cVal.mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | PCC |  | Phase to ground/phase to neutral three phase currents. | float | A | R | change & integrity | PCC |  | MMXU | A | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Phase to ground/phase to neutral real powers P. | float | W | R | change & integrity | PCC |  | MMXU | W | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Phase to ground/phase to neutral reactive powers Q. | float | Var | R | change & integrity | PCC |  | MMXU | VAr | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Phase to ground/phase to neutral apparent powers S. | float | VA | R | change & integrity | PCC |  | MMXU | VA | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Phase to ground/phase to neutral signed power factors. | float | / | R | change & integrity | PCC |  | MMXU | PF | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Phase to ground/phase to neutral impedances in a three-phase system. | float | ohm | R | change & integrity | PCC |  | MMXU | Z | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Rate of change of frequency | float | Hz/s | R | change & integrity | PCC |  | MMXU | HzRte | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Arithmetic average of the magnitude of current of the 3 phases: average(Ia,Ib,Ic). | float | A | R | change & integrity | PCC |  | MMXU | AvAPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Arithmetic average of the magnitude of phase to phase voltage of the 3 phases: average(PPVa, PPVb, PPVc). | float | V | R | change & integrity | PCC |  | MMXU | AvPPVPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Arithmetic average of the magnitude of phase to reference voltage of the 3 phases: average(PhVa, PhVb, PhVc). | float | V | R | change & integrity | PCC |  | MMXU | AvPhVPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Arithmetic average of the magnitude of active power of the 3 phases: average(Wa, Wb, Wc). | float | W | R | change & integrity | PCC |  | MMXU | AvWPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Arithmetic average of the magnitude of apparent power of the 3 phases: average(VAa, VAb, VAc). | float | Var | R | change & integrity | PCC |  | MMXU | AvVAPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Arithmetic average of the magnitude of reactive power of the 3 phases: average(VAra, VArb, VArc). | float | VA | R | change & integrity | PCC |  | MMXU | AvVArPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Arithmetic average of the magnitude of power factor of the 3 phases: average(PFa, PFb, PFc). | float | / | R | change & integrity | PCC |  | MMXU | AvPFPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Arithmetic average of the magnitude of impedance of the 3 phases: average(Za, Zb, Zc). | float | ohm | R | change & integrity | PCC |  | MMXU | AvZPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PCC |  | meter vendor | character | / | R | Initial | PCC |  | MMTR | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
MEAS_VAL | PCC |  | meter software version | character | / | R | Initial | PCC |  | MMTR | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
MEAS_VAL | PCC |  | meter description | character | / | R | Initial | PCC |  | MMTR | NamPlt | LPL | d | DC |  | IEC 61850 | THU
MEAS_VAL | PCC |  | meter configuration revision | character | / | R | Initial | PCC |  | MMTR | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Net apparent energy since last reset. | integer | VAh | R | change & integrity | PCC |  | MMTR | TotVAh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Net real energy since last reset. | integer | Wh | R | change & integrity | PCC |  | MMTR | TotWh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Net reactive energy since last reset. | integer | VArh | R | change & integrity | PCC |  | MMTR | TotVArh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Real energy supply (default direction: towards busbar). | integer | Wh | R | change & integrity | PCC |  | MMTR | SupWh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Reactive energy supply (default direction: towards busbar). | integer | VArh | R | change & integrity | PCC |  | MMTR | SupVArh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Real energy demand (direction: from busbar). | integer | Wh | R | change & integrity | PCC |  | MMTR | DmdWh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | PCC |  | Reactive energy demand (direction: from busbar). | integer | VArh | R | change & integrity | PCC |  | MMTR | DmdVArh | BCR | actVal | ST |  | IEC 61850 | THU
HW_META | PV-panel |  | Panel UUID | xy | / |  | Initial | [8 empty] | others | FIB |  |  | x
HW_META | PV-panel |  | Type panel | xy | / |  | Initial | [8 empty] | others | FIB |  |  | x | [8 empty] | x
HW_META | PV-panel |  | Panel azimut angle | xy | / |  | Initial | [8 empty] | others | FIB |  |  | x | [8 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Panel elevation angle | xy | / |  | Initial | [8 empty] | others | FIB |  |  | x | [8 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | panel power | xy |  |  | Initial | [8 empty] | others | FIB | [11 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Device nameplate (e.g. JKM530M-72HL4-BDVP) (DPVM, data object name: EEName) - OPTIONAL | character |  | R | Initial | [8 empty] | IEC 61850 | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Latitude (six decimal places) (DPVM, data object name: EEName) - MUST | float |  | R | Initial | [8 empty] | IEC 61850 | SGIS | [11 empty] | x | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Longitude (six decimal places) (DPMV, data object name: EEName) - MUST | float |  | R | Initial | [8 empty] | IEC 61850 | SGIS | [11 empty] | x | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Bifaciality factor (between 0 and 1, the ratio of rear efficiency in relation to the front efficiency) - MUST (if bifacial modules are used) | float |  | R | Initial | [8 empty] | others | SGIS | [11 empty] | x | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Module rated power at watts peak STC (DPVM, data object name: MdulWRtg) - MUST | float | Wp | R | Initial | [8 empty] | IEC 61850 | SGIS | [11 empty] | x | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Technology: e.g. monoSi, polySi, CdTe, mtHIT (Heterojunction with Intrinsic Thin layer solar cell), …OPTIONAL | character |  | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Length of a PV module - OPTIONAL | float | m | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Width of a PV module - OPTIONAL | float | m | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Thickness of a PV module - OPTIONAL | float | m | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Number of cells in series - OPTIONAL | unsigned integer |  | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Number of cells in parallel - OPTIONAL | unsigned integer |  | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Number of bypass diode - OPTIONAL | unsigned integer |  | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Cell arrea - OPTIONAL | float | m2 | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Nominal operating cell temperature (NOCT) - OPTIONAL | float | °C | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Module open circuit voltage (Voc at STC) (DPVM, data object name: MdulOcV) - OPTIONAL | float | V | R | Initial | [8 empty] | IEC 61850 | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Module short circuit current (Isc at STC) (DPVM, data object name: MdulScA) - OPTIONAL | float | A | R | Initial | [8 empty] | IEC 61850 | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Shunt resistance of a PV module - OPTIONAL | float | Ohm | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Series resistance of a PV module - OPTIONAL | float | Ohm | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Module current/temperature derate as percent of degrees above 25 ºC (DPVM, data object name: MdulATmpDrt) - OPTIONAL | float | %/°C | R | Initial | [8 empty] | IEC 61850 | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Number of bypass diodes - OPTIONAL | unsigned integer |  | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Module age derate as percent over time (DPVM, data object name: MdulDrtPct) - OPTIONAL | float | %/year | R | Initial | [8 empty] | IEC 61850 | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
HW_META | PV-panel |  | Diode ideality (quality) factor - OPTIONAL | float |  | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
SW_META | ECP |  | Name plate of the logical node | character | / | R | Initial | PV |  | LLN0 | NamPlt | LPL | vendor | DC |  | thucls | THU
SW_META | ECP |  | Name plate of the logical node | character | / | R | Initial | PV |  | LLN0 | NamPlt | LPL | swRev | DC |  | thucls | THU
SW_META | ECP |  | Name plate of the logical node | character | / | R | Initial | PV |  | LLN0 | NamPlt | LPL | d | DC |  | thucls | THU
SW_META | ECP |  | A placeholder for later use | character | / | R | Initial | PV |  | LLN0 | NamPlt | LPL | configRev | DC |  | thucls | THU
STAT_INFO | ECP |  | ECP data service failure description | character | / | R | Change | PV |  | LLN0 | Beh | ENS | d | DC |  | thucls | THU
SW_META | ECP |  | ECP service provider | character | / | R | Initial | PV |  | DECP | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
SW_META | ECP |  | ECP service software version | character | / | R | Initial | PV |  | DECP | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
SW_META | ECP |  | ECP service description | character | / | R | Initial | PV |  | DECP | NamPlt | LPL | d | DC |  | IEC 61850 | THU
SW_META | ECP |  | A placeholder for later use | character | / | R | Initial | PV |  | DECP | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
STAT_INFO | ECP |  | Type of circuit phases | enumeration | / | R | Initial | PV |  | DECP | PhsConnTyp | ENS | stVal | ST | PhaseKind | IEC 61850 | THU
SETTING | ECP |  | Default reference voltage for functions using voltage at this ECP as input | float | V | R/W | change | PV |  | DECP | VRef | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Percent of VRef to use in calculating the voltage to use in operational function calculations | float | % | R/W | change | PV |  | DECP | VRefPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Electrical active power rating at ECP | float | W | R/W | change | PV |  | DECP | WRtg | ASG | setMag | SP |  | others | SGIS
SETTING | ECP |  | Reactive power rating at ECP | float | Var | R/W | change | PV |  | DECP | VArRtg | ASG | setMag | SP |  | others | SGIS
SETTING | ECP |  | Apparent power rating at ECP | float | VA | R/W | change | PV |  | DECP | VARtg | ASG | setMag | SP |  | others | SGIS
SETTING | ECP |  | Voltage rating at ECP | float | V | R/W | change | PV |  | DECP | VRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Nominal frequency at ECP | float | Hz | R/W | change | PV |  | DECP | HzNom | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Rated maximum voltage | float | V | R/W | change | PV |  | DECP | VMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Rated minimum voltage | float | V | R/W | change | PV |  | DECP | Vmin | ASG | setMag | SP |  | IEC 61850 | THU
CTRL_PARA | ECP |  | Identity of electrical reference point as a Visible String | character | / | R/W | change | PV |  | DECP | ElcRefId | VSG | setVal | SP |  | IEC 61850 | THU
CTRL_PARA | ECP |  | Indication whether the active power from the DER referencing this ECP is included in the measurements coming from the ECP. This is important for managing Generation and Load Following, as well as Peak Power Limiting functions. | boolean | / | R | change | PV |  | DECP | DERMsIncl | SPG | setVal | SP |  | IEC 61850 | THU
CTRL_PARA | ECP |  | Reference to electrical measurement/calculation function, typically MMXU, MMXN or MMDC, MMTR LN instances | objectReference | / | R/W | change | PV |  | DECP | ElcMsRef | ORG | setSrcRef | SP |  | IEC 61850 | THU
HW_META | PV-Inverter |  | PV inverter name | character | / | R | Initial | PV |  | DGEN | EEName | DPL | name | DC |  | IEC 61850 | THU
HW_META | PV-Inverter |  | PV inverter hardware vendor | character | / | R | Initial | PV |  | DGEN | EEName | DPL | vendor | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | PV-Inverter |  | PV inverter hardware model | character | / | R | Initial | PV |  | DGEN | EEName | DPL | model | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | PV-Inverter |  | PV inverter hardware serial number | character | / | R | Initial | PV |  | DGEN | EEName | DPL | serNum | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
SW_META | PV-Inverter |  | PV inverter software revision | character | / | R | Initial | PV |  | DGEN | EEName | DPL | swRev | DC |  | thucls | THU |  |  |  |  | x
HW_META | PV-Inverter |  | PV inverter owner | character | / | R | Initial | PV |  | DGEN | EEName | DPL | owner | DC |  | IEC 61850 | THU
HW_META | PV-Inverter |  | PV inverter connected electrical power system | character | / | R | Initial | PV |  | DGEN | EEName | DPL | ePSName | DC |  | IEC 61850 | THU
HW_META | PV-Inverter |  | PV inverter primary operator | character | / | R | Initial | PV |  | DGEN | EEName | DPL | primeOper | DC |  | IEC 61850 | THU
HW_META | PV-Inverter |  | PV inverter secondary operator | character | / | R | Initial | PV |  | DGEN | EEName | DPL | secondOper | DC |  | IEC 61850 | THU
STAT_INFO | PV-Inverter |  | PV inverter hardware reversion | character | / | R | Change | PV |  | DGEN | EEName | DPL | hwRev | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
STAT_INFO | PV-Inverter |  | PV inverter hardware UUID | character | / | R | Initial | PV |  | DGEN | EEName | DPL | mRID | DC |  | IEC 61850 | FIB |  |  |  |  | x |  |  |  | x
STAT_INFO | PV-Inverter |  | PV inverter hardware description | character | / | R | Change | PV |  | DGEN | EEName | DPL | d | DC |  | IEC 61850 | THU |  |  |  |  | x |  |  |  | x
STAT_INFO | PV-Inverter |  | Name plate of the logical node | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
STAT_INFO | PV-Inverter |  | Name plate of the logical node | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
STAT_INFO | PV-Inverter |  | Name plate of the logical node | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | d | DC |  | IEC 61850 | THU
STAT_INFO | PV-Inverter |  | A placeholder for later use | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
STAT_INFO | PV-Inverter |  | PV inverter hardware failure description | character | / | R | Change | PV |  | DGEN | Beh | ENS | d | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
STAT_INFO | PV-Inverter |  | Current state of operation of the distributed energy resource. | enumeration | / | R | Change | PV |  | DGEN | DEROpSt | ENS | stVal | ST | DERStateKind | IEC 61850 | THU
STAT_INFO | PV-Inverter |  | Operation time of the external (electrical, mechanical or communication) equipment since start of the operation. | integer | h | R | Change | PV |  | DGEN | OpTmh | INS | stVal | ST |  | IEC 61850 | THU
STAT_INFO | PV-Inverter |  | State of external (electrical, mechanical or communication) equipment to which the logical node is associated. | enumeration | / | R | Change | PV |  | DGEN | EEHealth | ENS | stVal | ST | HealthKind | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | The calculation of the maximum power that the generator could output, based on constraining environmental conditions (e.g. solar insolation or wind speed or constraints from heat or vibrations). The delta between this calculation and the actual power being output indicates how much additional power could be output. | float | / | R | change & integrity | PV |  | DGEN | CnstWMax | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Total energy generated | float | Wh | R | change & integrity | PV |  | DGEN | GnEnTot | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Energy generated during the period since last reset | float | Wh | R | change & integrity | PV |  | DGEN | GnEnPer | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | The total amount of reactive power available for absorbing even if possibly impacting active power output (the use of this DO is mutually exclusive with the use of VArTot) | float | VAr | R | change & integrity | PV |  | DGEN | AvarTot | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | The total amount of reactive power available for injecting even if possibly impacting active power output (the use of this DO is mutually exclusive with the use of VArTot) | float | VAr | R | change & integrity | PV |  | DGEN | IvarTot | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | The amount of reactive power available for absorbing without impacting active power output (the use of this DO is mutually exclusive with the use of VArAvl) | float | VAr | R | change & integrity | PV |  | DGEN | AvarAvl | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | The amount of reactive power available for injecting without impacting active power output (the use of this DO is mutually exclusive with the use of VArAvl) | float | VAr | R | change & integrity | PV |  | DGEN | IvarAvl | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | Actual self service energy used | float | Wh | R | change & integrity | PV |  | DGEN | SelfSvcWh | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Actual percentage of apparent power output based on VAMax | float | % | R | change & integrity | PV |  | DGEN | VAPct | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | Available capability (measured or calculated) for increasing active output, including increasing generation of active power, even if currently consuming power. | float | W | R | change & integrity | PV |  | DGEN | AvlUpW | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | Available capability (measured or calculated) for decreasing active power, including increasing the consumption of active power, even if currently generating power. | float | W | R | change & integrity | PV |  | DGEN | AvlDnW | MV | mag | MX |  | IEC 61850 | THU
STAT_INFO | PV-Inverter |  | The number of times that the DER unit has been turned on or returned to service: count of "DER unit on" times, since the last time the counter was reset | unsigned integer | / | R | change | PV |  | DGEN | GnOnCnt | INC | stVal | ST |  | IEC 61850 | THU
STAT_INFO | PV-Inverter |  | Count of total number of starts | unsigned integer | / | R | change | PV |  | DGEN | TotStrCnt | INC | stVal | ST |  | IEC 61850 | THU
STAT_INFO | PV-Inverter |  | Count of starts in period since reset | unsigned integer | / | R | change | PV |  | DGEN | PerStrCnt | INC | stVal | ST |  | IEC 61850 | THU
STAT_INFO | PV-Inverter |  | Total time DER unit has operated – resettable: accumulated time since the last time the time was reset | integer | s | R | change | PV |  | DGEN | OpTms | INC | stVal | ST |  | IEC 61850 | THU
CTRL_PARA | PV-Inverter |  | (controllable) Operating with the value expressed in ctlVal (selected among the list specified in DERStateControlKind) initiates the appropriate transition request. The reading of its attribute stVal is meaningless. The resulting state of the DER shall be observed in the DEROpSt DO. | enumeration | / | W | change | PV |  | DGEN | DEROpStCtl | ENC | ctlVal |  | DERStateTransitionKind | IEC 61850 | THU
CTRL_PARA | PV-Inverter |  | Active power setpoint | float | W | W | change | PV |  | DGEN | WSpt | APC | ctlVal |  |  | thucls | THU
CTRL_PARA | PV-Inverter |  | Requested active power setpoint | float | W | R | change & integrity | PV |  | DGEN | WSpt | APC | mxVal | MX |  | thucls | THU
CTRL_PARA | PV-Inverter |  | Reactive power setpoint | float | VAr | W | change | PV |  | DGEN | VArSpt | APC | ctlVal |  |  | thucls | THU
CTRL_PARA | PV-Inverter |  | Requested reactive power setpoint | float | VAr | R | change & integrity | PV |  | DGEN | VArSpt | APC | mxVal | MX |  | thucls | THU
STAT_INFO | PV-Inverter |  | (controllable) Operations count, can be reset to a value different than 0. | integer | / | R/W | change | PV |  | DGEN | OpCntRs | INC | stVal | ST |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Value of power factor defined by a network operator - MUST. DGEN defines over-/under-excited power factor, could these be used? | float | / | R | change | [8 empty] | others | SGIS | [11 empty] | x | x | bar: interlink with other working packages T6.5
SETTING | PV-Inverter |  | Nameplate maximum active generation power rating at unity power factor | float | W | R/W | change | PV |  | DGEN | WMaxRtg | ASG | setMag | SP |  | IEC 61850 | SGIS
SETTING | PV-Inverter |  | Nameplate maximum apparent power generation rating | float | VA | R/W | change | PV |  | DGEN | VAMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Rating for maximum absorbing reactive power | float | VAr | R/W | change | PV |  | DGEN | AvarMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Rating for maximum supply (injection) reactive power | float | VAr | R/W | change | PV |  | DGEN | IvarMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Maximum current rating under nominal voltage under nominal power factor | float | A | R/W | change | PV |  | DGEN | AMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Maximum voltage rating | float | V | R/W | change | PV |  | DGEN | VMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Minimum voltage rating | float | V | R/W | change | PV |  | DGEN | VMinRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Maximum generation active power ramp up rating | float | W | R/W | change | PV |  | DGEN | WRpuMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Maximum generation active power ramp down rating | float | W | R/W | change | PV |  | DGEN | WRpdMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Max rated active power (WMaxRtg) which may result from controllable resource, .i.e whose level can be potentially controlled/set under the request of an entity external to the given DER. | float | W | R/W | change | PV |  | DGEN | CtbWMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Max rated reactive power VArMaxRtg, which may result from controllable resource, .i.e whose level can be potentially controlled/set under the request of an entity external to the given DER. | float | VAr | R/W | change | PV |  | DGEN | CtbVArMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Setting for maximum active power | float | W | R/W | change | PV |  | DGEN | WMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Default ramp rate for changes in active power: percentage of WMax per second | float | % | R/W | change | PV |  | DGEN | WRmp | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Setting for maximum absorbing reactive power (the use of this DO is mutually exclusive with the use of VArMax) | float | VAr | R/W | change | PV |  | DGEN | AvarMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Setting for maximum supply (injection) reactive power (the use of this DO is mutually exclusive with the use of VArMax) | float | VAr | R/W | change | PV |  | DGEN | IvarMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Setting for maximum voltage operational rating | float | V | R/W | change | PV |  | DGEN | VMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Setting for minimum voltage operational rating | float | V | R/W | change | PV |  | DGEN | VMin | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Setting for maximum operational current rating under nominal voltage under nominal power factor | float | A | R/W | change | PV |  | DGEN | AMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Setting for maximum absorbing apparent power (the use of this DO is mutually exclusive with the use of VAMax) | float | VA | R/W | change | PV |  | DGEN | AvaMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Setting for maximum injecting apparent power (the use of this DO is mutually exclusive with the use of VAMax) | float | VA | R/W | change | PV |  | DGEN | IvaMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Reference for reactive power setpoints. Selects which setpoint is active. | enumeration | / | R/W | change | PV |  | DGEN | VArSptRef | ENG | setVal | SP | ReactivePowerRefParamKind | IEC 61850 | THU
SETTING | PV-Inverter |  | Connection type of ECP: connection to DER (Point of Connection (PoC)), to load, within Local Electric Power System (Local EPS), Point of Common Coupling (PCC), or directly to Area EPS | enumeration | / | R/W | Initial | PV |  | DGEN | EcpConnTyp | ENG | setVal | SP | ECPConnKind | IEC 61850 | THU
SETTING | PV-Inverter |  | Phase type of electrical connection of the DER | enumeration | / | R/W | change | PV |  | DGEN | PhsConnTyp | ENG | setVal | SP | PhaseKind | IEC 61850 | THU
SETTING | PV-Inverter |  | Type of DER | enumeration | / | R/W | change | PV |  | DGEN | DERTyp | ENG | setVal | SP | DERUnitKind | IEC 61850 | THU
SETTING | PV-Inverter |  | Maximum temperature rating | float | °C | R/W | change | PV |  | DGEN | TmpMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Exposure to fault rates as percent of ?? | float | % | R/W | change | PV |  | DGEN | FltRtgPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Max fault current rating | float | A | R/W | change | PV |  | DGEN | FltAMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Max fault duration rating | float | ms | R/W | change | PV |  | DGEN | FltDurMaxTms | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Selfservice nominal power | float | W | R/W | change | PV |  | DGEN | SelfWRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Selfservice voltage | float | V | R/W | change | PV |  | DGEN | SelfVRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Selfservice nominal power factor | float | / | R/W | change | PV |  | DGEN | SelfPFRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Sequence (direction) reversed: False = ABC, true = CBA | boolean | / | R/W | change | PV |  | DGEN | RvSeq | SPG | setVal | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Efficiency at rated capacity as percent | float | % | R/W | change | PV |  | DGEN | EfcRtgPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Rated Nominal frequency of usage of the DER | float | Hz | R/W | change | PV |  | DGEN | HzNomRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Rated minimal frequency of usage of the DER | float | Hz | R/W | change | PV |  | DGEN | HzMinRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Rated maximum frequency of usage of the DER | float | Hz | R/W | change | PV |  | DGEN | HzMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Internal identifier of the resource within a system which is using that resource. It complements the mRID defined as part of the EEname DO. Different DERIds may be defined for different system users. | character | / | R/W | change | PV |  | DGEN | DERId | VSG | setVal | SP |  | IEC 61850 | THU
STAT_INFO | PV-Inverter |  | Name plate of the logical node | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | vendor | DC |  | thucls | THU
STAT_INFO | PV-Inverter |  | Name plate of the logical node | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | swRev | DC |  | thucls | THU
STAT_INFO | PV-Inverter |  | Name plate of the logical node | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | d | DC |  | thucls | THU
STAT_INFO | PV-Inverter |  | A placeholder for later use | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | configRev | DC |  | thucls | THU
STAT_INFO | PV-Inverter |  | Alarm trigger status: Inverter detects loss of AC power | character | / | R | change | PV |  | DINV | InvACLosAlm | SPS | stVal | ST |  | IEC 61850 | THU
STAT_INFO | PV-Inverter |  | Alarm trigger status: Inverter detects loss of DC power | character | / | R | change | PV |  | DINV | InvDCLosAlm | SPS | stVal | ST |  | IEC 61850 | THU
STAT_INFO | PV-Inverter |  | Alarm trigger status: Inverter detects loss of grid power | character | / | R | change | PV |  | DINV | InvGriLosAl | SPS | stVal | ST |  | IEC 61850 | THU
| PV-Inverter |  | Operation time of the external (electrical, mechanical or communication) equipment since start of the operation. | integer | h | R | change | PV |  | DINV | OpTmh | INS | stVal | ST |  | thucls | THU
CTRL_PARA | PV-Inverter |  | Active power setpoint of the inverter | float | W | W | change | PV |  | DINV | WSpt | APC | ctlVal |  |  | thucls | THU
CTRL_PARA | PV-Inverter |  | Requested active power setpoint of the inverter | float | W | R | change & integrity | PV |  | DINV | WSpt | APC | mxVal | MX |  | thucls | THU
CTRL_PARA | PV-Inverter |  | Reactive power setpoint of the inverter | float | VAr | W | change | PV |  | DINV | VArSpt | APC | ctlVal |  |  | thucls | THU
CTRL_PARA | PV-Inverter |  | Requested reactive power setpoint of the inverter | float | VAr | R | change & integrity | PV |  | DINV | VArSpt | APC | mxVal | MX |  | thucls | THU
SETTING | PV-Inverter |  | Inverter control source: current, voltage, voltagecurrent | enumeration | / | R/W | change | PV |  | DINV | InvCtlSrc | ENG | setVal | SP | InverterControlSourceKind | IEC 61850 | THU
SETTING | PV-Inverter |  | Rated active power of the inverter | float | W | R/W | change | PV |  | DINV | WRtg | ASG | setMag | SP |  | thucls | THU
SETTING | PV-Inverter |  | The continuous apparent power capability of the power inverter. | float | VAr | R/W | change | PV |  | DINV | VARtg | ASG | setMag | SP |  | IEC 61850 | THU
CTRL_PARA | PV-Inverter |  | PQV set of limiting curves. | Curve | / | R/W | change | PV |  | DINV | WVArVLim | CSG |  |  |  | IEC 61850 | THU
CTRL_PARA | PV-Inverter |  | Active curve characteristic curve for PQV limit. | Curve | / | R/W | change | PV |  | DINV | WVArVLimSet | CSG |  |  |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Nominal frequency of switching. | float | Hz | R/W | change | PV |  | DINV | SwHz | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | PV-Inverter |  | Type of isolation. | enumeration |  |  |  | PV |  | DINV | IsoTyp | ENG | setVal | SP | isolationKind | IEC 61850 | THU
SETTING | PV-Inverter |  | Type of AC system. | enumeration | W | R | initial | PV |  | DINV | ACTyp | ENG | setVal | SP | ACSystemKind | thucls | THU |  | x |  |  | x |  |  |  | x
SETTING | PV-Inverter |  | Maximum Input current limit. | float | A | R | initial | PV |  | DINV | InAMax | ENG | setVal | SP |  | thucls | THU | x | x |  |  | x |  |  |  | x
SETTING | PV-Inverter |  | Maximum Input voltage limit. | float | V | R | Change | PV |  | DINV | InVMax | ASG | setVal | SP |  | thucls | THU |  |  |  |  | x |  |  |  | x
SETTING | PV-Inverter |  | Rated bidirectional reactive power. | float | / | R | Change | PV |  | DINV | VArRtg | ASG | setVal | SP |  | thucls | THU | x |  |  |  | x |  |  |  | x
SETTING | PV-Inverter |  | Rated voltage (intrinsic property) | float | V | R/W | Change | PV |  | DINV | VRtg | ASG | setVal | SP |  | thucls | THU |  |  |  |  | x |  |  |  | x
OTHER | PV-Inverter |  | Pdc0, DC power level at which the AC power rating is achieved at the reference operating condition - OPTIONAL | float | W | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
OTHER | PV-Inverter |  | Vdc0, DC voltage level at which the AC power rating is achieved at reference operating conditions - OPTIONAL | float | V | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
OTHER | PV-Inverter |  | Ps0, DC power required to start the inversion process, or self-consumption by inverter, strongly influences inverter efficiency at low power levels - OPTIONAL | float | W | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
OTHER | PV-Inverter |  | C0, Parameter defining the curvature of the relationship between AC output power and DC input power - OPTIONAL | float |  | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
OTHER | PV-Inverter |  | C1, Parameter defining the curvature of the relationship between AC output power and DC input power - OPTIONAL | float |  | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
OTHER | PV-Inverter |  | C2, Parameter defining the curvature of the relationship between AC output power and DC input power - OPTIONAL | float |  | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
OTHER | PV-Inverter |  | C3, Parameter defining the curvature of the relationship between AC output power and DC input power - OPTIONAL | float |  | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
OTHER | PV-Inverter |  | Pnt, Night power consumption. - OPTIONAL | float | W | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
OTHER | PV-Inverter |  | Number of MPPT inputs. - OPTIONAL | unsigned integer |  | R | Initial | [8 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
FLEX_INFO | PV-Inverter |  | A list of flexibility market partner ID | character | / |  | Initial | PV |  | DCCT | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | A list of flexibility purchaser priority | character | / |  | Initial | PV |  | DCCT | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | Registered flexibility platform | character | / |  | Initial | PV |  | DCCT | NamPlt | LPL | d | DC |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | Currently activated flexibility purchaser | character | / |  | Initial | PV |  | DCCT | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | ISO 4217 currency 3-character code | character | / |  | change | PV |  | DCCT | Ccy | CUG | cur | SP |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | Marginal operational cost per hour | float | cur |  | change | PV |  | DCCT | OpCost | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | Marginal operational cost per kWh | float | cur |  | change | PV |  | DCCT | OpWhCost | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | Cost to start up DER | float | cur |  | change | PV |  | DCCT | StrCost | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | Cost to stop DER | float | cur |  | change | PV |  | DCCT | StopCost | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | Cost to ramp DER per kW per minute | float | cur |  | change | PV |  | DCCT | RampCost | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | Incremental heat rate piecewise linear curve costs. | Curve | / |  | change | PV |  | DCCT | HeatRteCost | CSG |  |  |  | IEC 61850 | THU
FLEX_INFO | PV-Inverter |  | Incremental carbon emission curve costs. | Curve | / |  | change | PV |  | DCCT | CRteCost | CSG |  |  |  | IEC 61850 | THU
MKT_IF | PV-Inverter |  | A list of energy market partner ID | character | / |  | Initial | PV |  | DCST | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
MKT_IF | PV-Inverter |  | A list of energy purchaser priority | character | / |  | Initial | PV |  | DCST | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
MKT_IF | PV-Inverter |  | Registered energy platform | character | / |  | Initial | PV |  | DCST | NamPlt | LPL | d | DC |  | IEC 61850 | THU
MKT_IF | PV-Inverter |  | Currently activated energy purchaser | character | / |  | Initial | PV |  | DCST | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
MKT_IF | PV-Inverter |  | ISO 4217 currency 3-character code | character | / |  | change | PV |  | DCST | Ccy | CUG | cur | SP |  | IEC 61850 | THU
MKT_IF | PV-Inverter |  | Cost to start up DER | float | cur |  | change | PV |  | DCST | StrCost | ASG | setMag | SP |  | IEC 61850 | THU
MKT_IF | PV-Inverter |  | Cost to stop DER | float | cur |  | change | PV |  | DCST | StopCost | ASG | setMag | SP |  | IEC 61850 | THU
MKT_IF | PV-Inverter |  | Cost to ramp DER per kW per minute | float | cur |  | change | PV |  | DCST | RampCost | ASG | setMag | SP |  | IEC 61850 | THU
MKT_IF | PV-Inverter |  | Incremental carbon emission curve costs. | Curve | / |  | change | PV |  | DCST | CRteCost | CSG |  |  |  | IEC 61850 | THU
MKT_IF | PV-Inverter |  | Active curve characteristics for the incremental heat rate curve | Curve | / |  | change | PV |  | DCST | HeatRteAct | CSG |  |  |  | IEC 61850 | THU
MKT_IF | PV-Inverter |  | Incremental heat rate piecewise linear curve costs. | Curve | / |  | change | PV |  | DCST | HeatRteCost | CSG |  |  |  | IEC 61850 | THU
HW_META | PV-Inverter |  | measuring unit vendor | character | / | R | Initial | PV |  | MMXU | NamPlt | LPL | vendor | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | PV-Inverter |  | measuring unit software version | character | / | R | Initial | PV |  | MMXU | NamPlt | LPL | swRev | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | PV-Inverter |  | measuring unit description | character | / | R | Initial | PV |  | MMXU | NamPlt | LPL | d | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | PV-Inverter |  | A placeholder for later use | character | / | R | Initial | PV |  | MMXU | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
STAT_INFO | PV-Inverter |  | status of the power vector expressed through one of the 9 zones of the PQ diagram quadrant, based on the signing conventions set with PFSign and PFExt. | enumeration | / | R | change | PV |  | MMXU | PQSt | ENS | stVal | ST | QuadrantRunningStateKind | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | total active power measurement | float | W | R | change & integrity | PV |  | MMXU | TotW | MV | mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | PV-Inverter |  | total reactive power measurement | float | Var | R | change & integrity | PV |  | MMXU | TotVar | MV | mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | PV-Inverter |  | total apparent power measurement | float | VA | R | change & integrity | PV |  | MMXU | TotVA | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | ratio of the absolute active power to the apparent power | float | / | R | change & integrity | PV |  | MMXU | TotPF | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | frequency | float | Hz | R | change & integrity | PV |  | MMXU | Hz | MV | mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | PV-Inverter |  | Phase to phase voltages. | float | V | R | change & integrity | PV |  | MMXU | PPV | DEL | phsAB/BC/CA.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Phase to neutral voltages. | float | V | R | change & integrity | PV |  | MMXU | PNV | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Phase to ground (line) voltages. | float | V | R | change & integrity | PV |  | MMXU | PhV | WYE | phsA/B/C.cVal.mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | PV-Inverter |  | Phase to ground/phase to neutral three phase currents. | float | A | R | change & integrity | PV |  | MMXU | A | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Phase to ground/phase to neutral real powers P. | float | W | R | change & integrity | PV |  | MMXU | W | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Phase to ground/phase to neutral reactive powers Q. | float | Var | R | change & integrity | PV |  | MMXU | VAr | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Phase to ground/phase to neutral apparent powers S. | float | VA | R | change & integrity | PV |  | MMXU | VA | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Phase to ground/phase to neutral signed power factors. | float | / | R | change & integrity | PV |  | MMXU | PF | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Phase to ground/phase to neutral impedances in a three-phase system. | float | ohm | R | change & integrity | PV |  | MMXU | Z | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Rate of change of frequency | float | Hz/s | R | change & integrity | PV |  | MMXU | HzRte | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Arithmetic average of the magnitude of current of the 3 phases: average(Ia,Ib,Ic). | float | A | R | change & integrity | PV |  | MMXU | AvAPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Arithmetic average of the magnitude of phase to phase voltage of the 3 phases: average(PPVa, PPVb, PPVc). | float | V | R | change & integrity | PV |  | MMXU | AvPPVPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Arithmetic average of the magnitude of phase to reference voltage of the 3 phases: average(PhVa, PhVb, PhVc). | float | V | R | change & integrity | PV |  | MMXU | AvPhVPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Arithmetic average of the magnitude of active power of the 3 phases: average(Wa, Wb, Wc). | float | W | R | change & integrity | PV |  | MMXU | AvWPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Arithmetic average of the magnitude of apparent power of the 3 phases: average(VAa, VAb, VAc). | float | Var | R | change & integrity | PV |  | MMXU | AvVAPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Arithmetic average of the magnitude of reactive power of the 3 phases: average(VAra, VArb, VArc). | float | VA | R | change & integrity | PV |  | MMXU | AvVArPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Arithmetic average of the magnitude of power factor of the 3 phases: average(PFa, PFb, PFc). | float | / | R | change & integrity | PV |  | MMXU | AvPFPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Arithmetic average of the magnitude of impedance of the 3 phases: average(Za, Zb, Zc). | float | ohm | R | change & integrity | PV |  | MMXU | AvZPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | meter vendor | character | / | R | Initial | PV |  | MMTR | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | meter software version | character | / | R | Initial | PV |  | MMTR | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | meter description | character | / | R | Initial | PV |  | MMTR | NamPlt | LPL | d | DC |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | meter configuration revision | character | / | R | Initial | PV |  | MMTR | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Net apparent energy since last reset. | integer | VAh | R | change & integrity | PV |  | MMTR | TotVAh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Net real energy since last reset. | integer | Wh | R | change & integrity | PV |  | MMTR | TotWh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Net reactive energy since last reset. | integer | VArh | R | change & integrity | PV |  | MMTR | TotVArh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Real energy supply (default direction: towards busbar). | integer | Wh | R | change & integrity | PV |  | MMTR | SupWh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Reactive energy supply (default direction: towards busbar). | integer | VArh | R | change & integrity | PV |  | MMTR | SupVArh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Real energy demand (direction: from busbar). | integer | Wh | R | change & integrity | PV |  | MMTR | DmdWh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | PV-Inverter |  | Reactive energy demand (direction: from busbar). | integer | VArh | R | change & integrity | PV |  | MMTR | DmdVArh | BCR | actVal | ST |  | IEC 61850 | THU
SCHD_INFO | PV-Inverter |  | PV active power forecast schedule provider | character | / | R | Initial | PV | PVCTL_ | FSCH | NamPlt | LPL | vendor | DC |  | thucls | THU
SCHD_INFO | PV-Inverter |  | PV active power forecast schedule revision | character | / | R | Initial | PV | PVCTL_ | FSCH | NamPlt | LPL | swRev | DC |  | thucls | THU
SCHD_INFO | PV-Inverter |  | PV active power forecast schedule description | character | / | R | Initial | PV | PVCTL_ | FSCH | NamPlt | LPL | d | DC |  | thucls | THU
SCHD_INFO | PV-Inverter |  | A placeholder for later use | character | / | R | Initial | PV | PVCTL_ | FSCH | NamPlt | LPL | configRev | DC |  | thucls | THU
SCHD_INFO | PV-Inverter |  | State of this schedule | enumeration | / | R | change | PV | PVCTL_ | FSCH | SchdSt | ENS | stVal | ST | ScheduleStateKind | thucls | THU
SCHD_INFO | PV-Inverter |  | The current schedule entry of a running schedule. This is the Data-Instance-ID of the data object ValXXX (e.g. ValASG). As long as the schedule is not running the value shall be 0. | integer | / | R | change | PV | PVCTL_ | FSCH | SchdEntr | INS | stVal | ST |  | thucls | THU
SCHD_INFO | PV-Inverter |  | The time when the schedule started running. If the schedule is not running, the quality of the value is set to invalid. | timestamp | / | R | change | PV | PVCTL_ | FSCH | ActStrTm | TCS | stVal | ST |  | thucls | THU
SCHD_INFO | PV-Inverter |  | The next time when the schedule is planned/intented to start or re-start running. If no schedules are planned running, the quality of the value is set to invalid. | timestamp | / | R | change | PV | PVCTL_ | FSCH | NxtStrTm | TCS | stVal | ST |  | thucls | THU
SCHD_INFO | PV-Inverter |  | Enumeration reflecting the potential error which has happened at the latest Schedule Enabling request | enumeration | / | R | change | PV | PVCTL_ | FSCH | SchdEnaErr | ENS | stVal | ST | ScheduleEnablingErrorKind | thucls | THU
SCHD_INFO | PV-Inverter |  | Current value determined by the schedule. As long as the schedule is not running the quality of the value is invalid. The unit of this data shall be the same as the unit of the data object(s) ValASG | float | / | R | change | PV | PVCTL_ | FSCH | ValMV | MV | mag | MX |  | thucls | THU
SCHD_INFO | PV-Inverter |  | (controllable) Operating with value true initiates enable transition request according to the state diagram; operating with value false is ignored. The change of its status value is a local issue. | boolean | / | R/W | change | PV | PVCTL_ | FSCH | EnaReq | SPC | ctlVal |  |  | thucls | THU
SCHD_INFO | PV-Inverter |  | (controllable) Operating with value true initiates disable transition request according to the state diagram; operating with value false is ignored. The change of its status value is a local issue. | boolean | / | R/W | change | PV | PVCTL_ | FSCH | DsaReq | SPC | ctlVal |  |  | thucls | THU
SCHD_INFO | PV-Inverter |  | The priority relation of this schedule (0..n) with higher numbers superseding lower numbers. Shall be a positive value. If missing the default is zero. | unsigned integer | / | R/W | change | PV | PVCTL_ | FSCH | SchdPrio | ING | setVal | SP |  | thucls | THU
SCHD_INFO | PV-Inverter |  | The number of schedule entries that are valid out of the instantiated ValASG, ValING, ValSPG or ValENG. NumEntr shall be > 0. NumEntr is <= number of instantiated Val[ASG¦ING¦SPG¦ENG]'s | unsigned integer | / | R/W | change | PV | PVCTL_ | FSCH | NumEntr | ING | setVal | SP |  | thucls | THU
SCHD_INFO | PV-Inverter |  | The schedule interval duration in time entities as specified in the unit. The SIUnit is mandatory in this data object. The total duration of a schedule shall be (NumEntr x SchdIntv). | unsigned integer | s | R/W | change | PV | PVCTL_ | FSCH | SchdIntv | ING | setVal | SP |  | thucls | THU
SCHD_INFO | PV-Inverter |  | The ASG scheduled values (current value output as MV). Multiple entries should be possible. | float | / | R/W | change | PV | PVCTL_ | FSCH | ValASG | ASG | setMag | SP |  | thucls | THU
SCHD_INFO | PV-Inverter |  | Start time of the schedule in UTC time. | timestamp | / | R/W | change | PV | PVCTL_ | FSCH | StrTm | TSG | setTm | SP |  | thucls | THU
SCHD_INFO | PV-Inverter |  | If true, the change of the schedule to the running and activated state is triggered by an external event and not by the start time. The external event is referenced through 'InSyn'. | boolean | / | R/W | change | PV | PVCTL_ | FSCH | EvtTrg | SPG | setVal | SP |  | thucls | THU
SCHD_INFO | PV-Inverter |  | Object reference of the external trigger if the schedule is triggered by an event. | objectReference | / | R/W | change | PV | PVCTL_ | FSCH | InSyn | ORG | setSrcRef | SP |  | thucls | THU
SCHD_INFO | PV-Inverter |  | If true, once terminated or disabled, the schedule will change to the validated state, otherwise it will change to the not ready state. | boolean | / | R/W | change | PV | PVCTL_ | FSCH | SchdReuse | SPG | setVal | SP |  | thucls | THU
SCHD_INFO | PV-Inverter |  | Object reference of data object bound to the input n. | objectReference | / | R/W | change | PV | PVCTL_ | FSCH | InRef | ORG | setSrcRef | SP |  | thucls | THU
SCHD_INFO | PV-Inverter |  | PV active power forecast schedule controller manager | character | / | R | Initial | PV | PVCTL_ | FSCC | NamPlt | LPL | vendor | DC |  | thucls | THU
SCHD_INFO | PV-Inverter |  | PV active power forecast schedule controller revision | character | / | R | Initial | PV | PVCTL_ | FSCC | NamPlt | LPL | swRev | DC |  | thucls | THU
SCHD_INFO | PV-Inverter |  | PV active power forecast schedule controller description | character | / | R | Initial | PV | PVCTL_ | FSCC | NamPlt | LPL | d | DC |  | thucls | THU
SCHD_INFO | PV-Inverter |  | A placeholder for later use | character | / | R | Initial | PV | PVCTL_ | FSCC | NamPlt | LPL | configRev | DC |  | thucls | THU
SCHD_INFO | PV-Inverter |  | Indication of which schedule is active as an object reference. As long as no schedule is active the quality of the value is invalid. The active schedule is selected by the schedule controller within the running schedules based on the priority of the running schedules. | objectReference | / | R | change | PV | PVCTL_ | FSCC | ActSchdRef | ORS | stVal | ST |  | thucls | THU
SCHD_INFO | PV-Inverter |  | Current value determined by the schedule. As long as the schedule is not running the quality of the value shall be set to invalid. The unit of this data shall be the same as the unit of the data object(s) FSCH.ValASG. | float | W | R | change | PV | PVCTL_ | FSCC | ValMV | MV | mag | MX |  | thucls | THU
SCHD_INFO | PV-Inverter |  | Object reference to the entity controlled by the schedule. | objectReference | / | R/W | change | PV | PVCTL_ | FSCC | CtlEnt | ORG | setSrcRef | SP |  | thucls | THU
SCHD_INFO | PV-Inverter |  | Object reference of schedule n (an LN reference to the LN of class FSCH). | objectReference | / | R/W | change | PV | PVCTL_ | FSCC | Schd | ORG | setSrcRef | SP |  | thucls | THU
SCHD_INFO | PV-Inverter |  | Object reference of data object bound to the input n. | objectReference | / | R/W | change | PV | PVCTL_ | FSCC | InRef | ORG | setSrcRef | SP |  | thucls | THU
SW_META | ECP |  | Name plate of the logical node | character | / | R | Initial | STO |  | LLN0 | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
SW_META | ECP |  | Name plate of the logical node | character | / | R | Initial | STO |  | LLN0 | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
SW_META | ECP |  | Name plate of the logical node | character | / | R | Initial | STO |  | LLN0 | NamPlt | LPL | d | DC |  | IEC 61850 | THU
SW_META | ECP |  | A placeholder for later use | character | / | R | Initial | STO |  | LLN0 | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
STAT_INFO | ECP |  | ECP data service failure description | character | / | R | Change | STO |  | LLN0 | Beh | ENS | d | DC |  | IEC 61850 | THU
SW_META | ECP |  | ECP service provider | character | / | R | Initial | STO |  | DECP | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
SW_META | ECP |  | ECP service software version | character | / | R | Initial | STO |  | DECP | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
SW_META | ECP |  | ECP service description | character | / | R | Initial | STO |  | DECP | NamPlt | LPL | d | DC |  | IEC 61850 | THU
SW_META | ECP |  | A placeholder for later use | character | / | R | Initial | STO |  | DECP | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
STAT_INFO | ECP |  | Type of circuit phases | enumeration | / | R | Initial | STO |  | DECP | PhsConnTyp | ENS | stVal | ST | PhaseKind | IEC 61850 | THU
SETTING | ECP |  | Default reference voltage for functions using voltage at this ECP as input | float | V | R/W | change | STO |  | DECP | VRef | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Percent of VRef to use in calculating the voltage to use in operational function calculations | float | % | R/W | change | STO |  | DECP | VRefPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Electrical active power rating at ECP | float | W | R/W | change | STO |  | DECP | WRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Reactive power rating at ECP | float | Var | R/W | change | STO |  | DECP | VArRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Apparent power rating at ECP | float | VA | R/W | change | STO |  | DECP | VARtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Voltage rating at ECP | float | V | R/W | change | STO |  | DECP | VRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Nominal frequency at ECP | float | Hz | R/W | change | STO |  | DECP | HzNom | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Rated maximum voltage | float | V | R/W | change | STO |  | DECP | VMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Rated minimum voltage | float | V | R/W | change | STO |  | DECP | Vmin | ASG | setMag | SP |  | IEC 61850 | THU
CTRL_PARA | ECP |  | Identity of electrical reference point as a Visible String | character | / | R/W | change | STO |  | DECP | ElcRefId | VSG | setVal | SP |  | IEC 61850 | THU
CTRL_PARA | ECP |  | Indication whether the active power from the DER referencing this ECP is included in the measurements coming from the ECP. This is important for managing Generation and Load Following, as well as Peak Power Limiting functions. | boolean | / | R | change | STO |  | DECP | DERMsIncl | SPG | setVal | SP |  | IEC 61850 | THU
HW_META | Electrical storage |  | Storage system name | character | / | R | Initial | STO |  | DSTO | EEName | DPL | name | DC |  | IEC 61850 | THU
HW_META | Electrical storage |  | Storage system hardware vendor | character | / | R | Initial | STO |  | DSTO | EEName | DPL | vendor | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | Electrical storage |  | Storage system hardware model | character | / | R | Initial | STO |  | DSTO | EEName | DPL | model | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | Electrical storage |  | Storage system hardware serial number | character | / | R | Initial | STO |  | DSTO | EEName | DPL | serNum | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
SW_META | Electrical storage |  | Storage system software revision | character | / | R | Initial | STO |  | DSTO | EEName | DPL | swRev | DC |  | thucls | THU |  |  |  |  | x
HW_META | Electrical storage |  | Storage system owner | character | / | R | Initial | STO |  | DSTO | EEName | DPL | owner | DC |  | IEC 61850 | THU
HW_META | Electrical storage |  | Storage system connected electrical power system | character | / | R | Initial | STO |  | DSTO | EEName | DPL | ePSName | DC |  | IEC 61850 | THU
HW_META | Electrical storage |  | Storage system primary operator | character | / | R | Initial | STO |  | DSTO | EEName | DPL | primeOper | DC |  | IEC 61850 | THU
HW_META | Electrical storage |  | Storage system secondary operator | character | / | R | Initial | STO |  | DSTO | EEName | DPL | secondOper | DC |  | IEC 61850 | THU
STAT_INFO | Electrical storage |  | Storage system hardware reversion | character | / | R | Change | STO |  | DSTO | EEName | DPL | hwRev | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
STAT_INFO | Electrical storage |  | Storage system hardware UUID | character | / | R | Initial | STO |  | DSTO | EEName | DPL | mRID | DC |  | IEC 61850 | FIB |  |  |  |  | x |  |  |  | x
STAT_INFO | Electrical storage |  | Storage system hardware description | character | / | R | Change | STO |  | DSTO | EEName | DPL | d | DC |  | IEC 61850 | THU |  |  |  |  | x |  |  |  | x
STAT_INFO | Electrical storage |  | Name plate of the logical node | character | / | R | Initial | STO |  | DSTO | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
STAT_INFO | Electrical storage |  | Name plate of the logical node | character | / | R | Initial | STO |  | DSTO | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
STAT_INFO | Electrical storage |  | Name plate of the logical node | character | / | R | Initial | STO |  | DSTO | NamPlt | LPL | d | DC |  | IEC 61850 | THU
STAT_INFO | Electrical storage |  | A placeholder for later use | character | / | R | Initial | STO |  | DSTO | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
STAT_INFO | Electrical storage |  | Alarm trigger status: if true, the maximum state of charge threshold of the battery (SocHiAlsPct) has been exceeded | boolean | / | R | change | STO |  | DSTO | SocHiAlm | SPS | stVal | ST |  | IEC 61850 | THU
STAT_INFO | Electrical storage |  | Warning trigger status: if true, the high state of charge warning threshold of the battery has been exceeded | boolean | / | R | change | STO |  | DSTO | SocHiWrn | SPS | stVal | ST |  | IEC 61850 | THU
STAT_INFO | Electrical storage |  | Alarm trigger status: If true,the minimum state of charge threshold of the battery (SocLoAlsPct) has been exceeded | boolean | / | R | change | STO |  | DSTO | SocLoAlm | SPS | stVal | ST |  | IEC 61850 | THU
STAT_INFO | Electrical storage |  | Warning trigger status: if true, the low state of charge warning threshold of the battery has been exceeded | boolean | / | R | change | STO |  | DSTO | SocLoWrn | SPS | stVal | ST |  | IEC 61850 | THU
STAT_INFO | Electrical storage |  | Alarm trigger status: If true, the predefined threshold of the low state of health of the storage resource (SohLoAlsPct) has been reached | boolean | / | R | change | STO |  | DSTO | SohLoAlm | SPS | stVal | ST |  | IEC 61850 | THU
STAT_INFO | Electrical storage |  | Count of the number of equivalent full charge cycles | integer | / | R | change | STO |  | DSTO | ChaCycCnt | INS | stVal | ST |  | IEC 61850 | THU
STAT_INFO | Electrical storage |  | Current state of operation of the distributed energy resource. | enumeration | / | R | change | STO |  | DSTO | DEROpSt | ENS | stVal | ST | DERStateKind | IEC 61850 | THU
STAT_INFO | Electrical storage |  | State of external (electrical, mechanical or communication) equipment to which the logical node is associated. | enumeration | / | R | change | STO |  | DSTO | EEHealth | ENS | stVal | ST | HealthKind | IEC 61850 | THU
STAT_INFO | Electrical storage |  | Operation time of the external (electrical,mechanical or communication) equipment sincestart of the operation. | integer | h | R | change | STO |  | DSTO | OpTmh | INS | stVal | ST |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Available energy capacity to be charged (in Wh) | float | Wh | R | change | STO |  | DSTO | InWh | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Energy stored and available for discharging (in Wh) | float | Wh | R | change | STO |  | DSTO | OutWh | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | state of charge expressed in Wh | float | Wh | R | change | STO |  | DSTO | SocWh | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Usable state of charge (expressed as percent of total usable energy capacity UseWh) which may be directly measured or calculated | float | % | R | change | STO |  | DSTO | UseSocPct | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | State of charge as percentage in relation to the effective energy capacity of the storage resource with respect to the degradation so far (EffWh). | float | % | R | change | STO |  | DSTO | SocEffWhPct | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Total Energy Charged since last reset (in Wh) | float | Wh | R | change | STO |  | DSTO | ChaWhTot | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Total Energy Discharged since last reset | float | Wh | R | change | STO |  | DSTO | DschWhTot | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Available power | float | W | R | change | STO |  | DSTO | AvlDschW | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Available charging power | float | W | R | change | STO |  | DSTO | AvlChaW | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Actual volt-amps percentage charged based on ChaVAMax | float | % | R | change | STO |  | DSTO | ChaVAPct | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | available charging time | float | s | R | change | STO |  | DSTO | AvlChaWTm | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Available discharging time | float | s | R | change | STO |  | DSTO | AvlDschWTm | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | The total amount of reactive power available for absorbing even if possibly impacting active power output while charging | float | VAr | R | change | STO |  | DSTO | ChaAvarTot | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | The total amount of reactive power available for absorbing even if possibly impacting active power output while discharging. | float | VAr | R | change | STO |  | DSTO | DschAvarTot | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | The total amount of reactive power available for injecting even if possibly impacting active power output while charging | float | VAr | R | change | STO |  | DSTO | ChaIvarTot | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | The total amount of reactive power available for injecting even if possibly impacting active power output while discharging | float | VAr | R | change | STO |  | DSTO | DschIvarTot | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | The amount of reactive power available for absorbing without impacting active power output while charging | float | VAr | R | change | STO |  | DSTO | ChaAvarAvl | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | The amount of reactive power available for absorbing without impacting active power output while discharging | float | VAr | R | change | STO |  | DSTO | DschAvarAvl | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | The amount of reactive power available for injecting without impacting active power output while charging | float | VAr | R | change | STO |  | DSTO | ChaIvarAvl | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | The amount of reactive power available for injecting without impacting active power output while discharging | float | VAr | R | change | STO |  | DSTO | DschIvarAvl | MV | mag | MX |  | IEC 61850 | THU
STAT_INFO | Electrical storage |  | Effective actual total energy capacity (in Wh) provided by the storage resource. Due to degradation, the amount may be less than the rated total energy capacity (WhRtg). | float | Wh | R | change | STO |  | DSTO | EffWh | MV | mag | MX |  | IEC 61850 | THU
STAT_INFO | Electrical storage |  | Effective actual total energy capacity (expressed as percentage of WhRtg) provided by the storage resource. Due to degradation, the amount may be less than the rated total energy capacity (WhRtg). In case both WhEffCapPct and WhEffCap DOs are present in a same LN instance, the application shall ensure to keep the values of both DOs consistent. | float | % | R | change | STO |  | DSTO | EffWhPct | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Actual self service energy used | float | Wh | R | change | STO |  | DSTO | SelfSvcWh | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Actual percentage of apparent power output based on VAMax | float | % | R | change | STO |  | DSTO | VAPct | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Available capability (measured or calculated) for increasing active output, including increasing generation of active power, even if currently consuming power. | float | W | R | change | STO |  | DSTO | AvlUpW | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Available capability (measured or calculated) for decreasing active power, including increasing the consumption of active power, even if currently generating power. | float | W | R | change | STO |  | DSTO | AvlDnW | MV | mag | MX |  | IEC 61850 | THU
CTRL_PARA | Electrical storage |  | Operating with the value expressed in ctlVal (selected among the list specified in DERStateControlKind) initiates the appropriate transition request. The reading of its attribute stVal is meaningless. The resulting state of the DER shall be observed in the DEROpSt DO. | enumeration | / | W | change | STO |  | DSTO | DEROpStCtl | ENC |  |  | DERStateTransitionKind | IEC 61850 | THU
CTRL_PARA | Electrical storage |  | Active power setpoint. | float | W | W | change | STO |  | DSTO | WSpt | APC | ctlVal |  |  | IEC 61850 | THU
CTRL_PARA | Electrical storage |  | Active power setpoint that is requested. | float | W | R | change & integrity | STO |  | DSTO | WSpt | APC | mxVal | MX |  | IEC 61850 | THU
CTRL_PARA | Electrical storage |  | Reactive power setpoint. | float | VAr | W | change | STO |  | DSTO | VArSpt | APC | ctlVal |  |  | IEC 61850 | THU
CTRL_PARA | Electrical storage |  | Reactive power setpoint that is requested. | float | VAr | R | change & integrity | STO |  | DSTO | VArSpt | APC | mxVal | MX |  | IEC 61850 | THU
STAT_INFO | Electrical storage |  | Operations count, can be reset to a value different than 0. | integer | / | R | change | STO |  | DSTO | OpCntRs | INC | stVal | ST |  | IEC 61850 | THU
SETTING | Electrical storage |  | High state of charge alarm threshold of the battery (in percent) | float | % | R/W | change | STO |  | DSTO | SocHiAlsPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Warning high state of charge threshold of the battery (in percent) | float | % | R/W | change | STO |  | DSTO | SocHiWrsPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Low state of charge alarm threshold of the battery (in percent) | float | % | R/W | change | STO |  | DSTO | SocLoAlsPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Warning state of charge threshold of the battery (in percent) | float | % | R/W | change | STO |  | DSTO | SocLoWrsPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Threshold alarm setting of the usable lower limit of the storage resource (in % of the usable capacity of the storage element (in Wh) – CapWhUseRtg ) | float | % | R/W | change | STO |  | DSTO | SohLoAlsPct | ASG | setMag | SP |  | IEC 61850 | THU
CTRL_PARA | Electrical storage |  | Roundtrip efficiency [%] at nominal conditions | float | % | R/W | change | STO |  | DSTO | RntEffPct | ASG | setMag | SP |  | IEC 61850 | THU
CTRL_PARA | Electrical storage |  | Nameplate maximum active power rating while charging | float | W | R/W | change | STO |  | DSTO | ChaWMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate maximum active power rating while discharging | float | W | R/W | change | STO |  | DSTO | DschWMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate ramp rate for changes in active power while charging: percentage of WMax per second | float | W | R/W | change | STO |  | DSTO | ChaWRmpRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate ramp rate for changes in active power while discharging: percentage of WMax per second | float | W | R/W | change | STO |  | DSTO | DschWRmpRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate maximum apparent charging power rating | float | VA | R/W | change | STO |  | DSTO | ChaVAMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate maximum apparent discharging power rating | float | VA | R/W | change | STO |  | DSTO | DschVAMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate rating for maximum absorbing reactive power while charging | float | AVar | R/W | change | STO |  | DSTO | ChaAvarRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate rating for maximum absorbing reactive power while discharging | float | AVar | R/W | change | STO |  | DSTO | DschAvarRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate rating for maximum supply (injection) reactive power while charging | float | AVar | R/W | change | STO |  | DSTO | ChaIvarRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate rating for maximum supply (injection) reactive power while discharging | float | AVar | R/W | change | STO |  | DSTO | DschIvarRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate rating for maximum voltage while charging | float | V | R/W | change | STO |  | DSTO | ChaVMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate rating for maximum voltage while discharging | float | V | R/W | change | STO |  | DSTO | DschVMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate rating for minimum voltage while charging | float | V | R/W | change | STO |  | DSTO | ChaVMinRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate rating for minimum voltage while discharging | float | V | R/W | change | STO |  | DSTO | DschVMinRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate rating for maximum current under nominal voltage under nominal power factor while charging | float | A | R/W | change | STO |  | DSTO | ChaAMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate rating for maximum current under nominal voltage under nominal power factor while discharging | float | A | R/W | change | STO |  | DSTO | DschAMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate energy storage capacity rating in Wh | float | Wh | R/W | change | STO |  | DSTO | WhRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate maximum amount of energy (in Wh) to be stored in the storage resource for e.g. supporting long life and avoid faster degradation | float | Wh | R/W | change | STO |  | DSTO | WhMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Nameplate minimum amount of energy (in Wh) to be retained in the storage resource for e.g. supporting long life and avoid faster degradation or to ensure a reserve of energy stored for emergencies and other purposes. | float | Wh | R/W | change | STO |  | DSTO | WhMinRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Charging efficiency curve rating [% over SoC] | Curve | / | R/W | change | STO |  | DSTO | ChaEfcRtg | CSG |  |  |  | IEC 61850 | THU
SETTING | Electrical storage |  | Discharging efficiency curve rating [% over SoC] | Curve | / | R/W | change | STO |  | DSTO | DschEfcRtg | CSG |  |  |  | IEC 61850 | THU
SETTING | Electrical storage |  | Net Energy Metering (NEM) Policy Mode which establishes whether the DER qualifies as renewable. Mode A = Storage may charge from the grid but may not discharge to the grid (acts only as load). Mode B = Storage may not charge from the grid but may discharge to the grid (charges from local energy source). Mode C = Storage may charge or discharge from the grid at will / in response to commands for location where there are no NEM integrity concerns. | enumeration | / | R/W | change | STO |  | DSTO | ChaSrcRtg | ENG | setVal | SP | ChargeSourceKind | IEC 61850 | THU
SETTING | Electrical storage |  | Maximum active power while charging | float | W | R/W | change | STO |  | DSTO | ChaWMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Default ramp rate for changes in active power: percentage of WMax per second while charging | float | W | R/W | change | STO |  | DSTO | ChaWRmp | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Default ramp rate for changes in active power: percentage of WMax per second while discharging | float | W | R/W | change | STO |  | DSTO | DschWRmp | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Charging reactive power maximum | float | VAr | R/W | change | STO |  | DSTO | ChaVArMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Discharging reactive power maximum | float | VAr | R/W | change | STO |  | DSTO | DschVArMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Maximum apparent charging power | float | VA | R/W | change | STO |  | DSTO | ChaVAMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Operational setpoint for maximum apparent power while discharging | float | VA | R/W | change | STO |  | DSTO | DschVAMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Operational setpoint for maximum absorbing reactive power while charging | float | VAr | R/W | change | STO |  | DSTO | ChaAvarMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Operational setpoint for maximum absorbing reactive power while discharging | float | VAr | R/W | change | STO |  | DSTO | DschAvarMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Operational setpoint for maximum supply (injection) reactive power while charging | float | VAr | R/W | change | STO |  | DSTO | ChaIvarMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Operational setpoint for maximum supply (injection) reactive power while discharging | float | VAr | R/W | change | STO |  | DSTO | DschIvarMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Operational setting for maximum voltage while charging | float | V | R/W | change | STO |  | DSTO | ChaVMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Operational setpoint for maximum voltage while discharging | float | V | R/W | change | STO |  | DSTO | DschVMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Operational setting for minimum voltage while charging | float | V | R/W | change | STO |  | DSTO | ChaVMin | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Operational setpoint for minimum voltage while discharging | float | V | R/W | change | STO |  | DSTO | DschVMin | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Operational setting for maximum current under nominal voltage under nominal power factor while charging | float | A | R/W | change | STO |  | DSTO | ChaAMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Operational setpoint for maximum current under nominal voltage under nominal power factor while discharging | float | A | R/W | change | STO |  | DSTO | DschAMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Charging efficiency curve [% over SoC] | Curve | / | R/W | change | STO |  | DSTO | ChaEfc | CSG |  |  |  | IEC 61850 | THU
SETTING | Electrical storage |  | Discharging efficiency curve [% over SoC] | Curve | / | R/W | change | STO |  | DSTO | DschEfc | CSG |  |  |  | IEC 61850 | THU
SETTING | Electrical storage |  | The energy reserve level above which the storage system may be only be charged in emergency situations, expressed as a percentage of the usable capacity, WhUseCap. | float | % | R/W | change | STO |  | DSTO | UseWhMaxPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | The energy reserve level below which the storage system may be only be discharged in emergency situations, expressed as a percentage of the usable capacity, WhUseCap. | float | % | R/W | change | STO |  | DSTO | UseWhMinPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Operational setpoint for usable energy storage capacity in Wh | float | Wh | R/W | change | STO |  | DSTO | UseWh | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Net Energy Metering (NEM) Policy Mode which establishes whether the DER qualifies as renewable. Mode A = Storage may charge from the grid but may not discharge to the grid (acts only as load). Mode B = Storage may not charge from the grid but may discharge to the grid (charges from local energy source). Mode C = Storage may charge or discharge from the grid at will / in response to commands for location where there are no NEM integrity concerns. | enumeration | / | R/W | change | STO |  | DSTO | ChaSrc | ENG | setVal | SP | ChargeSourceKind | IEC 61850 | THU
SETTING | Electrical storage |  | Source of charging storage: True = charge from renewable sources only, False = charge from any sources | boolean | / | R/W | change | STO |  | DSTO | RenChaEna | SPG | setVal | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Connection type of ECP: connection to DER (Point of Connection (PoC)), to load, within Local Electric Power System (Local EPS), Point of Common Coupling (PCC), or directly to Area EPS | enumeration | / | R/W | change | STO |  | DSTO | EcpConnTyp | ENG | setVal | SP | ECPConnKind | IEC 61850 | THU
SETTING | Electrical storage |  | Phase type of electrical connection of the DER | enumeration | / | R/W | change | STO |  | DSTO | PhsConnTyp | ENG | setVal | SP | PhaseKind | IEC 61850 | THU
SETTING | Electrical storage |  | Type of DER | enumeration | / | R/W | change | STO |  | DSTO | DERTyp | ENG | setVal | SP | DERUnitKind | IEC 61850 | THU
SETTING | Electrical storage |  | Maximum temperature rating | float | °C | R/W | change | STO |  | DSTO | TmpMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Exposure to fault rates as percent of ?? | float | % | R/W | change | STO |  | DSTO | FltRtgPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Max fault current rating | float | A | R/W | change | STO |  | DSTO | FltAMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Selfservice voltage | float | V | R/W | change | STO |  | DSTO | SelfVRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Max fault duration rating | integer | ms | R/W | change | STO |  | DSTO | FltDurMaxTms | ING | setVal | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Efficiency at rated capacity as percent | float | % | R/W | change | STO |  | DSTO | EfcRtgPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Rated Nominal frequency of usage of the DER | float | Hz | R/W | change | STO |  | DSTO | HzNomRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Rated minimal frequency of usage of the DER | float | Hz | R/W | change | STO |  | DSTO | HzMinRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Rated maximal frequency of usage of the DER | float | Hz | R/W | change | STO |  | DSTO | HzMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Electrical storage |  | Internal identifier of the resource within a system which is using that resource. It complements the mRID defined as part of the EEname DO. Different DERIds may be defined for different system users. | character | / | R/W | change | STO |  | DSTO | DERId | VSG | setVal | SP |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | A list of flexibility market partner ID | character | / |  | Initial | STO |  | DCCT | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | A list of flexibility purchaser priority | character | / |  | Initial | STO |  | DCCT | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Registered flexibility platform | character | / |  | Initial | STO |  | DCCT | NamPlt | LPL | d | DC |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Currently activated flexibility purchaser | character | / |  | Initial | STO |  | DCCT | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | ISO 4217 currency 3-character code | character | / |  | change | STO |  | DCCT | Ccy | CUG | cur | SP |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Marginal operational cost per hour | float | cur |  | change | STO |  | DCCT | OpCost | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Marginal operational cost per kWh | float | cur |  | change | STO |  | DCCT | OpWhCost | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Cost to start up DER | float | cur |  | change | STO |  | DCCT | StrCost | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Cost to stop DER | float | cur |  | change | STO |  | DCCT | StopCost | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Cost to ramp DER per kW per minute | float | cur |  | change | STO |  | DCCT | RampCost | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Incremental heat rate piecewise linear curve costs. | Curve | / |  | change | STO |  | DCCT | HeatRteCost | CSG |  |  |  | IEC 61850 | THU
FLEX_INFO | Electrical storage |  | Incremental carbon emission curve costs. | Curve | / |  | change | STO |  | DCCT | CRteCost | CSG |  |  |  | IEC 61850 | THU
MKT_IF | Electrical storage |  | A list of energy market partner ID | character | / |  | Initial | STO |  | DCST | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
MKT_IF | Electrical storage |  | A list of energy purchaser priority | character | / |  | Initial | STO |  | DCST | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
MKT_IF | Electrical storage |  | Registered energy platform | character | / |  | Initial | STO |  | DCST | NamPlt | LPL | d | DC |  | IEC 61850 | THU
MKT_IF | Electrical storage |  | Currently activated energy purchaser | character | / |  | Initial | STO |  | DCST | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
MKT_IF | Electrical storage |  | ISO 4217 currency 3-character code | character | / |  | change | STO |  | DCST | Ccy | CUG | cur | SP |  | IEC 61850 | THU
MKT_IF | Electrical storage |  | Cost to start up DER | float | cur |  | change | STO |  | DCST | StrCost | ASG | setMag | SP |  | IEC 61850 | THU
MKT_IF | Electrical storage |  | Cost to stop DER | float | cur |  | change | STO |  | DCST | StopCost | ASG | setMag | SP |  | IEC 61850 | THU
MKT_IF | Electrical storage |  | Cost to ramp DER per kW per minute | float | cur |  | change | STO |  | DCST | RampCost | ASG | setMag | SP |  | IEC 61850 | THU
MKT_IF | Electrical storage |  | Incremental carbon emission curve costs. | Curve | / |  | change | STO |  | DCST | CRteCost | CSG |  |  |  | IEC 61850 | THU
MKT_IF | Electrical storage |  | Active curve characteristics for the incremental heat rate curve | Curve | / |  | change | STO |  | DCST | HeatRteAct | CSG |  |  |  | IEC 61850 | THU
MKT_IF | Electrical storage |  | Incremental heat rate piecewise linear curve costs. | Curve | / |  | change | STO |  | DCST | HeatRteCost | CSG |  |  |  | IEC 61850 | THU
HW_META | Electrical storage |  | measuring unit vendor | character | / | R | Initial | STO |  | MMXU | NamPlt | LPL | vendor | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | Electrical storage |  | measuring unit software version | character | / | R | Initial | STO |  | MMXU | NamPlt | LPL | swRev | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | Electrical storage |  | measuring unit description | character | / | R | Initial | STO |  | MMXU | NamPlt | LPL | d | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | Electrical storage |  | A placeholder for later use | character | / | R | Initial | STO |  | MMXU | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
STAT_INFO | Electrical storage |  | status of the power vector expressed through one of the 9 zones of the PQ diagram quadrant, based on the signing conventions set with PFSign and PFExt. | enumeration | / | R | change | STO |  | MMXU | PQSt | ENS | stVal | ST | QuadrantRunningStateKind | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | total active power measurement | float | W | R | change & integrity | STO |  | MMXU | TotW | MV | mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | Electrical storage |  | total reactive power measurement | float | Var | R | change & integrity | STO |  | MMXU | TotVar | MV | mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | Electrical storage |  | total apparent power measurement | float | VA | R | change & integrity | STO |  | MMXU | TotVA | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | ratio of the absolute active power to the apparent power | float | / | R | change & integrity | STO |  | MMXU | TotPF | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | frequency | float | Hz | R | change & integrity | STO |  | MMXU | Hz | MV | mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | Electrical storage |  | Phase to phase voltages. | float | V | R | change & integrity | STO |  | MMXU | PPV | DEL | phsAB/BC/CA.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Phase to neutral voltages. | float | V | R | change & integrity | STO |  | MMXU | PNV | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Phase to ground (line) voltages. | float | V | R | change & integrity | STO |  | MMXU | PhV | WYE | phsA/B/C.cVal.mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | Electrical storage |  | Phase to ground/phase to neutral three phase currents. | float | A | R | change & integrity | STO |  | MMXU | A | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Phase to ground/phase to neutral real powers P. | float | W | R | change & integrity | STO |  | MMXU | W | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Phase to ground/phase to neutral reactive powers Q. | float | Var | R | change & integrity | STO |  | MMXU | VAr | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Phase to ground/phase to neutral apparent powers S. | float | VA | R | change & integrity | STO |  | MMXU | VA | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Phase to ground/phase to neutral signed power factors. | float | / | R | change & integrity | STO |  | MMXU | PF | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Phase to ground/phase to neutral impedances in a three-phase system. | float | ohm | R | change & integrity | STO |  | MMXU | Z | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Rate of change of frequency | float | Hz/s | R | change & integrity | STO |  | MMXU | HzRte | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Arithmetic average of the magnitude of current of the 3 phases: average(Ia,Ib,Ic). | float | A | R | change & integrity | STO |  | MMXU | AvAPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Arithmetic average of the magnitude of phase to phase voltage of the 3 phases: average(PPVa, PPVb, PPVc). | float | V | R | change & integrity | STO |  | MMXU | AvPPVPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Arithmetic average of the magnitude of phase to reference voltage of the 3 phases: average(PhVa, PhVb, PhVc). | float | V | R | change & integrity | STO |  | MMXU | AvPhVPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Arithmetic average of the magnitude of active power of the 3 phases: average(Wa, Wb, Wc). | float | W | R | change & integrity | STO |  | MMXU | AvWPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Arithmetic average of the magnitude of apparent power of the 3 phases: average(VAa, VAb, VAc). | float | Var | R | change & integrity | STO |  | MMXU | AvVAPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Arithmetic average of the magnitude of reactive power of the 3 phases: average(VAra, VArb, VArc). | float | VA | R | change & integrity | STO |  | MMXU | AvVArPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Arithmetic average of the magnitude of power factor of the 3 phases: average(PFa, PFb, PFc). | float | / | R | change & integrity | STO |  | MMXU | AvPFPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Arithmetic average of the magnitude of impedance of the 3 phases: average(Za, Zb, Zc). | float | ohm | R | change & integrity | STO |  | MMXU | AvZPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | meter vendor | character | / | R | Initial | STO |  | MMTR | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | meter software version | character | / | R | Initial | STO |  | MMTR | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | meter description | character | / | R | Initial | STO |  | MMTR | NamPlt | LPL | d | DC |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | meter configuration revision | character | / | R | Initial | STO |  | MMTR | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Net apparent energy since last reset. | integer | VAh | R | change & integrity | STO |  | MMTR | TotVAh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Net real energy since last reset. | integer | Wh | R | change & integrity | STO |  | MMTR | TotWh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Net reactive energy since last reset. | integer | VArh | R | change & integrity | STO |  | MMTR | TotVArh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Real energy supply (default direction: towards busbar). | integer | Wh | R | change & integrity | STO |  | MMTR | SupWh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Reactive energy supply (default direction: towards busbar). | integer | VArh | R | change & integrity | STO |  | MMTR | SupVArh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Real energy demand (direction: from busbar). | integer | Wh | R | change & integrity | STO |  | MMTR | DmdWh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | Electrical storage |  | Reactive energy demand (direction: from busbar). | integer | VArh | R | change & integrity | STO |  | MMTR | DmdVArh | BCR | actVal | ST |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | PV active power forecast schedule provider | character | / | R | Initial | STO | STOCTL_ | FSCH | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | PV active power forecast schedule revision | character | / | R | Initial | STO | STOCTL_ | FSCH | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | PV active power forecast schedule description | character | / | R | Initial | STO | STOCTL_ | FSCH | NamPlt | LPL | d | DC |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | A placeholder for later use | character | / | R | Initial | STO | STOCTL_ | FSCH | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | State of this schedule | enumeration | / | R | change | STO | STOCTL_ | FSCH | SchdSt | ENS | stVal | ST | ScheduleStateKind | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | The current schedule entry of a running schedule. This is the Data-Instance-ID of the data object ValXXX (e.g. ValASG). As long as the schedule is not running the value shall be 0. | integer | / | R | change | STO | STOCTL_ | FSCH | SchdEntr | INS | stVal | ST |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | The time when the schedule started running. If the schedule is not running, the quality of the value is set to invalid. | timestamp | / | R | change | STO | STOCTL_ | FSCH | ActStrTm | TCS | stVal | ST |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | The next time when the schedule is planned/intented to start or re-start running. If no schedules are planned running, the quality of the value is set to invalid. | timestamp | / | R | change | STO | STOCTL_ | FSCH | NxtStrTm | TCS | stVal | ST |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | Enumeration reflecting the potential error which has happened at the latest Schedule Enabling request | enumeration | / | R | change | STO | STOCTL_ | FSCH | SchdEnaErr | ENS | stVal | ST | ScheduleEnablingErrorKind | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | Current value determined by the schedule. As long as the schedule is not running the quality of the value is invalid. The unit of this data shall be the same as the unit of the data object(s) ValASG | float | / | R | change | STO | STOCTL_ | FSCH | ValMV | MV | mag | MX |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | (controllable) Operating with value true initiates enable transition request according to the state diagram; operating with value false is ignored. The change of its status value is a local issue. | boolean | / | R/W | change | STO | STOCTL_ | FSCH | EnaReq | SPC | ctlVal |  |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | (controllable) Operating with value true initiates disable transition request according to the state diagram; operating with value false is ignored. The change of its status value is a local issue. | boolean | / | R/W | change | STO | STOCTL_ | FSCH | DsaReq | SPC | ctlVal |  |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | The priority relation of this schedule (0..n) with higher numbers superseding lower numbers. Shall be a positive value. If missing the default is zero. | unsigned integer | / | R/W | change | STO | STOCTL_ | FSCH | SchdPrio | ING | setVal | SP |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | The number of schedule entries that are valid out of the instantiated ValASG, ValING, ValSPG or ValENG. NumEntr shall be > 0. NumEntr is <= number of instantiated Val[ASG¦ING¦SPG¦ENG]'s | unsigned integer | / | R/W | change | STO | STOCTL_ | FSCH | NumEntr | ING | setVal | SP |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | The schedule interval duration in time entities as specified in the unit. The SIUnit is mandatory in this data object. The total duration of a schedule shall be (NumEntr x SchdIntv). | unsigned integer | s | R/W | change | STO | STOCTL_ | FSCH | SchdIntv | ING | setVal | SP |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | The ASG scheduled values (current value output as MV). Multiple entries should be possible. | float | / | R/W | change | STO | STOCTL_ | FSCH | ValASG | ASG | setMag | SP |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | Start time of the schedule in UTC time. | timestamp | / | R/W | change | STO | STOCTL_ | FSCH | StrTm | TSG | setTm | SP |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | If true, the change of the schedule to the running and activated state is triggered by an external event and not by the start time. The external event is referenced through 'InSyn'. | boolean | / | R/W | change | STO | STOCTL_ | FSCH | EvtTrg | SPG | setVal | SP |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | Object reference of the external trigger if the schedule is triggered by an event. | objectReference | / | R/W | change | STO | STOCTL_ | FSCH | InSyn | ORG | setSrcRef | SP |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | If true, once terminated or disabled, the schedule will change to the validated state, otherwise it will change to the not ready state. | boolean | / | R/W | change | STO | STOCTL_ | FSCH | SchdReuse | SPG | setVal | SP |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | Object reference of data object bound to the input n. | objectReference | / | R/W | change | STO | STOCTL_ | FSCH | InRef | ORG | setSrcRef | SP |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | PV active power forecast schedule controller manager | character | / | R | Initial | STO | STOCTL_ | FSCC | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | PV active power forecast schedule controller revision | character | / | R | Initial | STO | STOCTL_ | FSCC | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | PV active power forecast schedule controller description | character | / | R | Initial | STO | STOCTL_ | FSCC | NamPlt | LPL | d | DC |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | A placeholder for later use | character | / | R | Initial | STO | STOCTL_ | FSCC | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | Indication of which schedule is active as an object reference. As long as no schedule is active the quality of the value is invalid. The active schedule is selected by the schedule controller within the running schedules based on the priority of the running schedules. | objectReference | / | R | change | STO | STOCTL_ | FSCC | ActSchdRef | ORS | stVal | ST |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | Current value determined by the schedule. As long as the schedule is not running the quality of the value shall be set to invalid. The unit of this data shall be the same as the unit of the data object(s) FSCH.ValASG. | float | W | R | change | STO | STOCTL_ | FSCC | ValMV | MV | mag | MX |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | Object reference to the entity controlled by the schedule. | objectReference | / | R/W | change | STO | STOCTL_ | FSCC | CtlEnt | ORG | setSrcRef | SP |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | Object reference of schedule n (an LN reference to the LN of class FSCH). | objectReference | / | R/W | change | STO | STOCTL_ | FSCC | Schd | ORG | setSrcRef | SP |  | IEC 61850 | THU
SCHD_INFO | Electrical storage |  | Object reference of data object bound to the input n. | objectReference | / | R/W | change | STO | STOCTL_ | FSCC | InRef | ORG | setSrcRef | SP |  | IEC 61850 | THU
SW_META | ECP |  | Name plate of the logical node | character | / | R | Initial | LOAD |  | LLN0 | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
SW_META | ECP |  | Name plate of the logical node | character | / | R | Initial | LOAD |  | LLN0 | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
SW_META | ECP |  | Name plate of the logical node | character | / | R | Initial | LOAD |  | LLN0 | NamPlt | LPL | d | DC |  | IEC 61850 | THU
SW_META | ECP |  | A placeholder for later use | character | / | R | Initial | LOAD |  | LLN0 | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
STAT_INFO | ECP |  | ECP data service failure description | character | / | R | Change | LOAD |  | LLN0 | Beh | ENS | d | DC |  | IEC 61850 | THU
SW_META | ECP |  | ECP service provider | character | / | R | Initial | LOAD |  | DECP | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
SW_META | ECP |  | ECP service software version | character | / | R | Initial | LOAD |  | DECP | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
SW_META | ECP |  | ECP service description | character | / | R | Initial | LOAD |  | DECP | NamPlt | LPL | d | DC |  | IEC 61850 | THU
SW_META | ECP |  | A placeholder for later use | character | / | R | Initial | LOAD |  | DECP | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
STAT_INFO | ECP |  | Type of circuit phases | enumeration | / | R | Initial | LOAD |  | DECP | PhsConnTyp | ENS | stVal | ST | PhaseKind | IEC 61850 | THU
SETTING | ECP |  | Default reference voltage for functions using voltage at this ECP as input | float | V | R/W | change | LOAD |  | DECP | VRef | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Percent of VRef to use in calculating the voltage to use in operational function calculations | float | % | R/W | change | LOAD |  | DECP | VRefPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Electrical active power rating at ECP | float | W | R/W | change | LOAD |  | DECP | WRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Reactive power rating at ECP | float | Var | R/W | change | LOAD |  | DECP | VArRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Apparent power rating at ECP | float | VA | R/W | change | LOAD |  | DECP | VARtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Voltage rating at ECP | float | V | R/W | change | LOAD |  | DECP | VRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Nominal frequency at ECP | float | Hz | R/W | change | LOAD |  | DECP | HzNom | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Rated maximum voltage | float | V | R/W | change | LOAD |  | DECP | VMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | ECP |  | Rated minimum voltage | float | V | R/W | change | LOAD |  | DECP | Vmin | ASG | setMag | SP |  | IEC 61850 | THU
CTRL_PARA | ECP |  | Identity of electrical reference point as a Visible String | character | / | R/W | change | LOAD |  | DECP | ElcRefId | VSG | setVal | SP |  | IEC 61850 | THU
CTRL_PARA | ECP |  | Indication whether the active power from the DER referencing this ECP is included in the measurements coming from the ECP. This is important for managing Generation and Load Following, as well as Peak Power Limiting functions. | boolean | / | R | change | LOAD |  | DECP | DERMsIncl | SPG | setVal | SP |  | IEC 61850 | THU
HW_META | Load |  | Storage system name | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | name | DC |  | IEC 61850 | THU
HW_META | Load |  | Storage system hardware vendor | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | vendor | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | Load |  | Storage system hardware model | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | model | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | Load |  | Storage system hardware serial number | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | serNum | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
SW_META | Load |  | Storage system software revision | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | swRev | DC |  | thucls | THU |  |  |  |  | x
HW_META | Load |  | Storage system owner | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | owner | DC |  | IEC 61850 | THU
HW_META | Load |  | Storage system connected electrical power system | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | ePSName | DC |  | IEC 61850 | THU
HW_META | Load |  | Storage system primary operator | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | primeOper | DC |  | IEC 61850 | THU
HW_META | Load |  | Storage system secondary operator | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | secondOper | DC |  | IEC 61850 | THU
STAT_INFO | Load |  | Storage system hardware reversion | character | / | R | Change | LOAD |  | DLOD | EEName | DPL | hwRev | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
STAT_INFO | Load |  | Storage system hardware UUID | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | mRID | DC |  | IEC 61850 | FIB |  |  |  |  | x |  |  |  | x
STAT_INFO | Load |  | Storage system hardware description | character | / | R | Change | LOAD |  | DLOD | EEName | DPL | d | DC |  | IEC 61850 | THU |  |  |  |  | x |  |  |  | x
STAT_INFO | Load |  | Name plate of the logical node | character | / | R | Initial | LOAD |  | DLOD | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
STAT_INFO | Load |  | Name plate of the logical node | character | / | R | Initial | LOAD |  | DLOD | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
STAT_INFO | Load |  | Name plate of the logical node | character | / | R | Initial | LOAD |  | DLOD | NamPlt | LPL | d | DC |  | IEC 61850 | THU
STAT_INFO | Load |  | A placeholder for later use | character | / | R | Initial | LOAD |  | DLOD | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
STAT_INFO | Load |  | Current state of operation of the distributed energy resource. | enumeration | / | R | change & integrity | LOAD |  | DLOD | DEROpSt | ENS | stVal | ST | DERStateKind | IEC 61850 | THU
STAT_INFO | Load |  | State of external (electrical, mechanical or communication) equipment to which the logical node is associated. | enumeration | / | R | change | LOAD |  | DLOD | EEHealth | ENS | stVal | ST | HealthKind | IEC 61850 | THU
STAT_INFO | Load |  | Operation time of the external (electrical, mechanical or communication) equipment since start of the operation. | unsigned integer | h |  | integrity | LOAD |  | DLOD | OpTmh | INS | stVal | ST |  | IEC 61850 | THU
MEAS_VAL | Load |  | The total amount of reactive power available for absorbing even if possibly impacting active power output (the use of this DO is mutually exclusive with the use of VArTot) | float | VAr | R | change & integrity | LOAD |  | DLOD | AvarTot | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | The total amount of reactive power available for injecting even if possibly impacting active power output (the use of this DO is mutually exclusive with the use of VArTot) | float | VAr | R | change & integrity | LOAD |  | DLOD | IvarTot | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Load |  | The amount of reactive power available without impacting active power output if the distinction between absorbing and injecting reactive power is not significant (the use of this DO is mutually exclusive with the use of AvarAvl and IvarAvl) | float | VAr | R | change & integrity | LOAD |  | DLOD | VArAvl | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Load |  | The amount of reactive power available for absorbing without impacting active power output (the use of this DO is mutually exclusive with the use of VArAvl) | float | VAr | R | change & integrity | LOAD |  | DLOD | AvarAvl | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Load |  | The amount of reactive power available for injecting without impacting active power output (the use of this DO is mutually exclusive with the use of VArAvl) | float | VAr | R | change & integrity | LOAD |  | DLOD | IvarAvl | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Actual self service energy used | float | Wh | R | change & integrity | LOAD |  | DLOD | SelfSvcWh | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Actual percentage of apparent power output based on VAMax | float | % | R | change & integrity | LOAD |  | DLOD | VAPct | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Load |  | Available capability (measured or calculated) for increasing active output, including increasing generation of active power, even if currently consuming power. | float | W | R | change & integrity | LOAD |  | DLOD | AvlUpW | MV | mag | MX |  | IEC 61850 | THU
FLEX_INFO | Load |  | Available capability (measured or calculated) for decreasing active power, including increasing the consumption of active power, even if currently generating power. | float | W | R | change & integrity | LOAD |  | DLOD | AvlDnW | MV | mag | MX |  | IEC 61850 | THU
CTRL_PARA | Load |  | (controllable) Operating with the value expressed in ctlVal (selected among the list specified in DERStateControlKind) initiates the appropriate transition request. The reading of its attribute stVal is meaningless. The resulting state of the DER shall be observed in the DEROpSt DO. | enumeration | / | W | change | LOAD |  | DLOD | DEROpStCtl | ENC | ctlVal | MX | DERStateTransitionKi nd | IEC 61850 | THU
CTRL_PARA | Load |  | Active power setpoint. | float | W | W | change | LOAD |  | DLOD | WSpt | APC | ctlVal |  |  | IEC 61850 | THU
CTRL_PARA | Load |  | Active power setpoint that is requested. | float | W | R | change & integrity | LOAD |  | DLOD | WSpt | APC | mxVal | MX |  | IEC 61850 | THU
CTRL_PARA | Load |  | Reactive power setpoint. | float | VAr | W | change | LOAD |  | DLOD | VArSpt | APC | ctlVal |  |  | IEC 61850 | THU
CTRL_PARA | Load |  | Reactive power setpoint that is requested. | float | VAr | R | change & integrity | LOAD |  | DLOD | VArSpt | APC | mxVal | MX |  | IEC 61850 | THU
CTRL_PARA | Load |  | (controllable) Operations count, can be reset to a value different than 0. | unsigned integer | / | R/W | change | LOAD |  | DLOD | OpCntRs | INC | ctlVal |  |  | IEC 61850 | THU
SETTING | Load |  | Nameplate maximum Load active power rating at unity power factor | float | W | R/W | change | LOAD |  | DLOD | WMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Maximum voltage rating | float | V | R/W | change | LOAD |  | DLOD | VMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Minimum voltage rating | float | V | R/W | change | LOAD |  | DLOD | VMinRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Maximum current rating under nominal voltage under nominal power factor while charging | float | A | R/W | change | LOAD |  | DLOD | AMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Nameplate maximum apparent charging power rating | float | VA | R/W | change | LOAD |  | DLOD | VAMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Maximum nameplate charging ramp up rating | float | W | R/W | change | LOAD |  | DLOD | WRpuMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Maximum nameplate charging ramp down rating | float | W | R/W | change | LOAD |  | DLOD | WRpdMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Maximum nameplate charging ramp down rating | float | W | R/W | change | LOAD |  | DLOD | WMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Default ramp rate for changes in active power: percentage of WMax per second | float | W | R/W | change | LOAD |  | DLOD | WRmp | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Setting for maximum absorbing reactive power (the use of this DO is mutually exclusive with the use of VArMax) | float | VAr | R/W | change | LOAD |  | DLOD | AvarMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Setting for maximum supply (injection) reactive power (the use of this DO is mutually exclusive with the use of VArMax) | float | VAr | R/W | change | LOAD |  | DLOD | IvarMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Setting for maximum voltage operational rating | float | V | R/W | change | LOAD |  | DLOD | VMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Setting for minimum voltage operational rating | float | V | R/W | change | LOAD |  | DLOD | VMin | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Setting for maximum operational current rating under nominal voltage under nominal power factor | float | A | R/W | change | LOAD |  | DLOD | AMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Setting for maximum absorbing apparent power (the use of this DO is mutually exclusive with the use of VAMax) | float | VA | R/W | change | LOAD |  | DLOD | AvaMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Setting for maximum injecting apparent power (the use of this DO is mutually exclusive with the use of VAMax) | float | VA | R/W | change | LOAD |  | DLOD | IvaMax | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Reference for reactive power setpoints. Selects which setpoint is active. | enumeration | / | R/W | change | LOAD |  | DLOD | VArSptRef | ENG | setMag | SP | ReactivePowerRefPar amKind | IEC 61850 | THU
SETTING | Load |  | Connection type of ECP: connection to DER (Point of Connection (PoC)), to load, within Local Electric Power System (Local EPS), Point of Common Coupling (PCC), or directly to Area EPS | enumeration | / | R/W | change | LOAD |  | DLOD | EcpConnTyp | ENG | setVal | SP | ECPConnKind | IEC 61850 | THU
SETTING | Load |  | Phase type of electrical connection of the DER | enumeration | / | R/W | change | LOAD |  | DLOD | PhsConnTyp | ENG | setVal | SP | PhaseKind | IEC 61850 | THU
SETTING | Load |  | Type of DER | enumeration | / | R/W | change | LOAD |  | DLOD | DERTyp | ENG | setVal | SP | DERUnitKind | IEC 61850 | THU
SETTING | Load |  | Maximum temperature rating | float | °C | R/W | change | LOAD |  | DLOD | TmpMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Exposure to fault rates as percent of ?? | float | % | R/W | change | LOAD |  | DLOD | FltRtgPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Max fault current rating | float | A | R/W | change | LOAD |  | DLOD | FltAMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Selfservice voltage | float | V | R/W | change | LOAD |  | DLOD | SelfVRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Max fault duration rating | float | ms | R/W | change | LOAD |  | DLOD | FltDurMaxTms | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Selfservice nominal power | float | W | R/W | change | LOAD |  | DLOD | SelfWRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Selfservice nominal power factor | float | / | R/W | change | LOAD |  | DLOD | SelfPFRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Selfservice acceptable voltage range | float | V | R/W | change | LOAD |  | DLOD | SelfVRngRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Efficiency at rated capacity as percent | float | % | R/W | change | LOAD |  | DLOD | EfcRtgPct | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Rated Nominal frequency of usage of the DER | float | Hz | R/W | change | LOAD |  | DLOD | HzNomRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Rated minimal frequency of usage of the DER | float | Hz | R/W | change | LOAD |  | DLOD | HzMinRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Rated maximum frequency of usage of the DER | float | Hz | R/W | change | LOAD |  | DLOD | HzMaxRtg | ASG | setMag | SP |  | IEC 61850 | THU
SETTING | Load |  | Internal identifier of the resource within a system which is using that resource. It complements the mRID defined as part of the EEname DO. Different DERIds may be defined for different system users. | float | / | R/W | change | LOAD |  | DLOD | DERId | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | Load |  | A list of energy market partner ID | character | / |  | Initial | LOAD |  | DCCT | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
FLEX_INFO | Load |  | A list of energy purchaser priority | character | / |  | Initial | LOAD |  | DCCT | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
FLEX_INFO | Load |  | Registered energy platform | character | / |  | Initial | LOAD |  | DCCT | NamPlt | LPL | d | DC |  | IEC 61850 | THU
FLEX_INFO | Load |  | Currently activated energy purchaser | character | / |  | Initial | LOAD |  | DCCT | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
FLEX_INFO | Load |  | ISO 4217 currency 3-character code | character | / |  | change | LOAD |  | DCCT | Ccy | CUG | cur | SP |  | IEC 61850 | THU
FLEX_INFO | Load |  | Marginal operational cost per hour | float | cur |  | change | LOAD |  | DCCT | OpCost | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | Load |  | Marginal operational cost per kWh | float | cur |  | change | LOAD |  | DCCT | OpWhCost | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | Load |  | Cost to start up DER | float | cur |  | change | LOAD |  | DCCT | StrCost | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | Load |  | Cost to stop DER | float | cur |  | change | LOAD |  | DCCT | StopCost | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | Load |  | Cost to ramp DER per kW per minute | float | cur |  | change | LOAD |  | DCCT | RampCost | ASG | setMag | SP |  | IEC 61850 | THU
FLEX_INFO | Load |  | Incremental heat rate piecewise linear curve costs. | Curve | / |  | change | LOAD |  | DCCT | HeatRteCost | CSG |  |  |  | IEC 61850 | THU
FLEX_INFO | Load |  | Incremental carbon emission curve costs. | Curve | / |  | change | LOAD |  | DCCT | CRteCost | CSG |  |  |  | IEC 61850 | THU
MKT_IF | Load |  | Name plate of the logical node. | character | / |  | Initial | LOAD |  | DCST | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
MKT_IF | Load |  | Name plate of the logical node. | character | / |  | Initial | LOAD |  | DCST | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
MKT_IF | Load |  | Name plate of the logical node. | character | / |  | Initial | LOAD |  | DCST | NamPlt | LPL | d | DC |  | IEC 61850 | THU
MKT_IF | Load |  | Name plate of the logical node. | character | / |  | Initial | LOAD |  | DCST | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
MKT_IF | Load |  | ISO 4217 currency 3-character code | character | / |  | change | LOAD |  | DCST | Ccy | CUG | cur | SP |  | IEC 61850 | THU
MKT_IF | Load |  | Cost to start up DER | float | cur |  | change | LOAD |  | DCST | StrCost | ASG | setMag | SP |  | IEC 61850 | THU
MKT_IF | Load |  | Cost to stop DER | float | cur |  | change | LOAD |  | DCST | StopCost | ASG | setMag | SP |  | IEC 61850 | THU
MKT_IF | Load |  | Cost to ramp DER per kW per minute | float | cur |  | change | LOAD |  | DCST | RampCost | ASG | setMag | SP |  | IEC 61850 | THU
MKT_IF | Load |  | Incremental carbon emission curve costs. | Curve | / |  | change | LOAD |  | DCST | CRteCost | CSG |  |  |  | IEC 61850 | THU
MKT_IF | Load |  | Active curve characteristics for the incremental heat rate curve | Curve | / |  | change | LOAD |  | DCST | HeatRteAct | CSG |  |  |  | IEC 61850 | THU
MKT_IF | Load |  | Incremental heat rate piecewise linear curve costs. | Curve | / |  | change | LOAD |  | DCST | HeatRteCost | CSG |  |  |  | IEC 61850 | THU
HW_META | Load |  | measuring unit vendor | character | / | R | Initial | LOAD |  | MMXU | NamPlt | LPL | vendor | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | Load |  | measuring unit software version | character | / | R | Initial | LOAD |  | MMXU | NamPlt | LPL | swRev | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | Load |  | measuring unit description | character | / | R | Initial | LOAD |  | MMXU | NamPlt | LPL | d | DC |  | thucls | THU |  |  |  |  | x |  |  |  | x
HW_META | Load |  | A placeholder for later use | character | / | R | Initial | LOAD |  | MMXU | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
STAT_INFO | Load |  | status of the power vector expressed through one of the 9 zones of the PQ diagram quadrant, based on the signing conventions set with PFSign and PFExt. | enumeration | / | R | change | LOAD |  | MMXU | PQSt | ENS | stVal | ST | QuadrantRunningStateKind | IEC 61850 | THU
MEAS_VAL | Load |  | total active power measurement | float | W | R | change & integrity | LOAD |  | MMXU | TotW | MV | mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | Load |  | total reactive power measurement | float | Var | R | change & integrity | LOAD |  | MMXU | TotVar | MV | mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | Load |  | total apparent power measurement | float | VA | R | change & integrity | LOAD |  | MMXU | TotVA | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | ratio of the absolute active power to the apparent power | float | / | R | change & integrity | LOAD |  | MMXU | TotPF | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | frequency | float | Hz | R | change & integrity | LOAD |  | MMXU | Hz | MV | mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | Load |  | Phase to phase voltages. | float | V | R | change & integrity | LOAD |  | MMXU | PPV | DEL | phsAB/BC/CA.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Phase to neutral voltages. | float | V | R | change & integrity | LOAD |  | MMXU | PNV | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Phase to ground (line) voltages. | float | V | R | change & integrity | LOAD |  | MMXU | PhV | WYE | phsA/B/C.cVal.mag | MX |  | thucls | THU |  |  |  |  | x |  |  |  | x
MEAS_VAL | Load |  | Phase to ground/phase to neutral three phase currents. | float | A | R | change & integrity | LOAD |  | MMXU | A | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Phase to ground/phase to neutral real powers P. | float | W | R | change & integrity | LOAD |  | MMXU | W | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Phase to ground/phase to neutral reactive powers Q. | float | Var | R | change & integrity | LOAD |  | MMXU | VAr | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Phase to ground/phase to neutral apparent powers S. | float | VA | R | change & integrity | LOAD |  | MMXU | VA | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Phase to ground/phase to neutral signed power factors. | float | / | R | change & integrity | LOAD |  | MMXU | PF | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Phase to ground/phase to neutral impedances in a three-phase system. | float | ohm | R | change & integrity | LOAD |  | MMXU | Z | WYE | phsA/B/C.cVal.mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Rate of change of frequency | float | Hz/s | R | change & integrity | LOAD |  | MMXU | HzRte | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Arithmetic average of the magnitude of current of the 3 phases: average(Ia,Ib,Ic). | float | A | R | change & integrity | LOAD |  | MMXU | AvAPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Arithmetic average of the magnitude of phase to phase voltage of the 3 phases: average(PPVa, PPVb, PPVc). | float | V | R | change & integrity | LOAD |  | MMXU | AvPPVPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Arithmetic average of the magnitude of phase to reference voltage of the 3 phases: average(PhVa, PhVb, PhVc). | float | V | R | change & integrity | LOAD |  | MMXU | AvPhVPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Arithmetic average of the magnitude of active power of the 3 phases: average(Wa, Wb, Wc). | float | W | R | change & integrity | LOAD |  | MMXU | AvWPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Arithmetic average of the magnitude of apparent power of the 3 phases: average(VAa, VAb, VAc). | float | Var | R | change & integrity | LOAD |  | MMXU | AvVAPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Arithmetic average of the magnitude of reactive power of the 3 phases: average(VAra, VArb, VArc). | float | VA | R | change & integrity | LOAD |  | MMXU | AvVArPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Arithmetic average of the magnitude of power factor of the 3 phases: average(PFa, PFb, PFc). | float | / | R | change & integrity | LOAD |  | MMXU | AvPFPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | Arithmetic average of the magnitude of impedance of the 3 phases: average(Za, Zb, Zc). | float | ohm | R | change & integrity | LOAD |  | MMXU | AvZPhs | MV | mag | MX |  | IEC 61850 | THU
MEAS_VAL | Load |  | meter vendor | character | / | R | Initial | LOAD |  | MMTR | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
MEAS_VAL | Load |  | meter software version | character | / | R | Initial | LOAD |  | MMTR | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
MEAS_VAL | Load |  | meter description | character | / | R | Initial | LOAD |  | MMTR | NamPlt | LPL | d | DC |  | IEC 61850 | THU
MEAS_VAL | Load |  | meter configuration revision | character | / | R | Initial | LOAD |  | MMTR | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
MEAS_VAL | Load |  | Net apparent energy since last reset. | integer | VAh | R | change & integrity | LOAD |  | MMTR | TotVAh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | Load |  | Net real energy since last reset. | integer | Wh | R | change & integrity | LOAD |  | MMTR | TotWh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | Load |  | Net reactive energy since last reset. | integer | VArh | R | change & integrity | LOAD |  | MMTR | TotVArh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | Load |  | Real energy supply (default direction: towards busbar). | integer | Wh | R | change & integrity | LOAD |  | MMTR | SupWh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | Load |  | Reactive energy supply (default direction: towards busbar). | integer | VArh | R | change & integrity | LOAD |  | MMTR | SupVArh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | Load |  | Real energy demand (direction: from busbar). | integer | Wh | R | change & integrity | LOAD |  | MMTR | DmdWh | BCR | actVal | ST |  | IEC 61850 | THU
MEAS_VAL | Load |  | Reactive energy demand (direction: from busbar). | integer | VArh | R | change & integrity | LOAD |  | MMTR | DmdVArh | BCR | actVal | ST |  | IEC 61850 | THU
SW_META | data interface |  | Meteorological data provider | character | / | R | Initial | METEO |  | LLN0 | NamPlt | LPL | vendor | DC |  | IEC 61850 | THU
SW_META | data interface |  | Meteorological data version | character | / | R | Initial | METEO |  | LLN0 | NamPlt | LPL | swRev | DC |  | IEC 61850 | THU
SW_META | data interface |  | Meteorological datadescription | character | / | R | Initial | METEO |  | LLN0 | NamPlt | LPL | d | DC |  | IEC 61850 | THU
SW_META | data interface |  | A placeholder for later use | character | / | R | Initial | METEO |  | LLN0 | NamPlt | LPL | configRev | DC |  | IEC 61850 | THU
STAT_INFO | data interface |  | Meteorological data failure description | character | / | R | Change | METEO |  | LLN0 | Beh | ENS | d | DC |  | IEC 61850 | THU
HW_META | data interface |  | Weather-station (if locally installed) name | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | name | DC |  | IEC 61850 | THU
HW_META | data interface |  | Weather-station (if locally installed) hardware vendor | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | vendor | DC |  | IEC 61850 | THU
HW_META | data interface |  | Weather-station (if locally installed) hardware model | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | model | DC |  | IEC 61850 | THU
HW_META | data interface |  | Weather-station (if locally installed) hardware serial number | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | serNum | DC |  | IEC 61850 | THU
SW_META | data interface |  | Weather-station (if locally installed) software revision | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | swRev | DC |  | IEC 61850 | THU
HW_META | data interface |  | Weather-station (if locally installed) location | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | location | DC |  | IEC 61850 | THU
HW_META | data interface |  | Weather-station (if locally installed) longitude, WGS84 coordinates | float | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | longitude | DC |  | IEC 61850 | THU
HW_META | data interface |  | Weather-station (if locally installed) latitude, WGS84 coordinates | float | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | latitude | DC |  | IEC 61850 | THU
HW_META | data interface |  | Weather-station (if locally installed) owner | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | owner | DC |  | IEC 61850 | THU
HW_META | data interface |  | Weather-station (if locally installed) connected electrical power system | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | ePSName | DC |  | IEC 61850 | THU
HW_META | data interface |  | Weather-station (if locally installed) primary operator | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | primeOper | DC |  | IEC 61850 | THU
HW_META | data interface |  | Weather-station (if locally installed) secondary operator | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | secondOper | DC |  | IEC 61850 | THU
STAT_INFO | data interface |  | Weather-station (if locally installed) hardware reversion | character | / | R | Change | METEO |  | LPHD | PhyNam | DPL | hwRev | DC |  | IEC 61850 | THU
STAT_INFO | data interface |  | Weather-station (if locally installed) hardware failure description | character | / | R | Change | METEO |  | LPHD | Beh | ENS | d | DC |  | IEC 61850 | THU
HW_META | data interface |  | vendor of meteorological sensor | character | / | R | Initial | METEO |  | MMET | NamPlt | LPL | vendor | DC |  | IEC 61850 | SGIS
SW_META | data interface |  | Software revision of meteorological sensor | character | / | R | Initial | METEO |  | MMET | NamPlt | LPL | swRev | DC |  | IEC 61850 | SGIS
HW_META | data interface |  | Type of meteorological sensor and its classification (A, B or C) acc. to ISO 9060 - OPTIONAL | character | / | R | Initial | METEO |  | MMET | NamPlt | LPL | d | DC |  | IEC 61850 | SGIS
HW_META | data interface |  | A placeholder for later use | character | / | R | Initial | METEO |  | MMET | NamPlt | LPL | configRev | DC |  | IEC 61850 | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
METEO_INFO | data interface |  | Total horizontal insolation - if it is available and reliable (MMET, Data object name: HorInsol) - OPTIONAL | float | W/m2 | R | change & integrity | METEO |  | MMET | HorInsol | MV | mag | MX |  | IEC 61850 | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
METEO_INFO | data interface |  | Direct normal insolation - if it is available and reliable (MMET, Data object name: DctInsol) - OPTIONAL | float | W/m2 | R | change & integrity | METEO |  | MMET | DctInsol | MV | mag | MX |  | IEC 61850 | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
METEO_INFO | data interface |  | Diffuse insolation - if it is available and reliable (MMET, Data object name: DffInsol) - OPTIONAL | float | W/m2 | R | change & integrity | METEO |  | MMET | DffInsol | MV | mag | MX |  | IEC 61850 | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
METEO_INFO | data interface |  | Ambient temperature - if it is available and reliable (MMET, Data object name: EnvTmp) - OPTIONAL | float | °C | R | change & integrity | METEO |  | MMET | EnvTmp | MV | mag | MX |  | IEC 61850 | SGIS | [11 empty] | x | x | bar: interlink with other working packages T6.5
METEO_INFO | data interface |  | Snowfall - if it is available and reliable (MMET, Data object name: SnwFll) - OPTIONAL | float | kg/m2 | R | change & integrity | METEO |  | MMET | SnwFll | MV | mag | MX |  | IEC 61850 | SGIS | [11 empty] | x | x | bar: interlink with other working packages T6.5
METEO_INFO | data interface |  | Snow cover - if it is available and reliable (MMET, Data object name: SnwCvr) - OPTIONAL | float | kg/m2 | R | change & integrity | METEO |  | MMET | SnwCvr | MV | mag | MX |  | IEC 61850 | SGIS | [11 empty] | x | x | bar: interlink with other working packages T6.5
METEO_INFO | data interface |  | Rainfall - if it is available and reliable (MMET, Data object name: RnFll) - OPTIONAL | float | kg/m2 | R | change & integrity | METEO |  | MMET | RnFll | MV | mag | MX |  | IEC 61850 | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
METEO_INFO | data interface |  | Humidity - relative humidity - if it is available and reliable (MMET, Data object name: EnvHum) - OPTIONAL | float | % | R | change & integrity | METEO |  | MMET | EnvHum | MV | mag | MX |  | IEC 61850 | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
METEO_INFO | data interface |  | Barometric pressure - athmospheric pressure - if it is available and reliable (MMET, Data object name: EnvPres) - OPTIONAL | float | hPa | R | change & integrity | METEO |  | MMET | EnvPres | MV | mag | MX |  | IEC 61850 | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
METEO_INFO | data interface |  | Horizontal Wind direction - if it is available and reliable (MMET, Data object name: HorWdDir - OPTIONAL | float | deg. | R | change & integrity | METEO |  | MMET | HorWdDir | MV | mag | MX |  | IEC 61850 | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
METEO_INFO | data interface |  | Horizontal Wind speed - if it is available and reliable (MMET, Data object name: HorWdSpd) - OPTIONAL | float | m/s | R | change & integrity | METEO |  | MMET | HorWdSpd | MV | mag | MX |  | IEC 61850 | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
METEO_INFO | data interface |  | Plane of array insolation (insolation SIUnit [W/m2]). | float | W/m2 | R | change & integrity | METEO |  | MMET | PoaInsol | MV | mag | MX |  | IEC 61850 | THU
METEO_INFO | data interface |  | Wet bulb temperature (typically in °C). | float | °C | R | change & integrity | METEO |  | MMET | WetBlbTmp | MV | mag | MX |  | IEC 61850 | THU
METEO_INFO | data interface |  | Cloud cover level. | float | / | R | change & integrity | METEO |  | MMET | CloudCvr | MV | mag | MX |  | IEC 61850 | THU
METEO_INFO | data interface |  | Dew point temperature | float | °C | R | change & integrity | METEO |  | MMET | DewPt | MV | mag | MX |  | IEC 61850 | THU
METEO_INFO | data interface |  | Daylight duration (time elapsed between sunrise and sunset). | float | h | R | change & integrity | METEO |  | MMET | DlDur | MV | mag | MX |  | IEC 61850 | THU
METEO_INFO | data interface |  | Vertical wind direction. | float | m/s | R | change & integrity | METEO |  | MMET | VerWdDir | MV | mag | MX |  | IEC 61850 | THU
METEO_INFO | data interface |  | Average vertical wind speed. | float | m/s | R | change & integrity | METEO |  | MMET | VerWdSpd | MV | mag | MX |  | IEC 61850 | THU
METEO_INFO | data interface |  | Maximum wind gust speed. | float | m/s | R | change & integrity | METEO |  | MMET | WdGustSpd | MV | mag | MX |  | IEC 61850 | THU
METEO_INFO | data interface |  | Snowfall density (typically in g/cm3 – density SIUnit [kg/m3]). | float | kg/m3 | R | change & integrity | METEO |  | MMET | SnwDen | MV | mag | MX |  | IEC 61850 | THU
METEO_INFO | data interface |  | Snowfall temperature (typically in °C). | float | °C | R | change & integrity | METEO |  | MMET | SnwTmp | MV | mag | MX |  | IEC 61850 | THU
|  |  | Water equivalent of snowfall (typically in mm – length SIUnit [m]). | float | m/s | R | change & integrity | METEO |  | MMET | SnwEq | MV | mag | MX |  | IEC 61850 | THU
METEO_INFO | data interface |  | Global Tilted Irradiation - total radiation received on a surface with defined tilt and azimuth, fixed or sun-tracking. Is this parameter PoaInsol in MMET? | float | W/m2 | R/W | change & integrity | METEO | [7 empty] | others | SGIS | [12 empty] | x | bar: interlink with other working packages T6.5
METEO_INFO | data interface |  | Pvout - estimated solar photovoltaic (PV) power generation. Representation as schedule. | float | W | R | change & integrity | METEO | [7 empty] | others | SGIS | [11 empty] | x | x | bar: interlink with other working packages T6.5
SCHD_INFO | data interface |  | PV active power forecast schedule provider | character | / | R | Initial | METEO | PVGEN_ | FSCH | NamPlt | LPL | vendor | DC |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | PV active power forecast schedule revision | character | / | R | Initial | METEO | PVGEN_ | FSCH | NamPlt | LPL | swRev | DC |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | PV active power forecast schedule description | character | / | R | Initial | METEO | PVGEN_ | FSCH | NamPlt | LPL | d | DC |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | A placeholder for later use | character | / | R | Initial | METEO | PVGEN_ | FSCH | NamPlt | LPL | configRev | DC |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | State of this schedule | enumeration | / | R | change | METEO | PVGEN_ | FSCH | SchdSt | ENS | stVal | ST | ScheduleStateKind | IEC 61850 | SGIS
SCHD_INFO | data interface |  | The current schedule entry of a running schedule. This is the Data-Instance-ID of the data object ValXXX (e.g. ValASG). As long as the schedule is not running the value shall be 0. | enumeration | / | R | change | METEO | PVGEN_ | FSCH | SchdEntr | INS | stVal | ST | ScheduleEnablingErrorKind | IEC 61850 | SGIS
SCHD_INFO | data interface |  | The time when the schedule started running. If the schedule is not running, the quality of the value is set to invalid. | timestamp | / | R | change | METEO | PVGEN_ | FSCH | ActStrTm | TCS | stVal | ST |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | The next time when the schedule is planned/intented to start or re-start running. If no schedules are planned running, the quality of the value is set to invalid. | timestamp | / | R | change | METEO | PVGEN_ | FSCH | NxtStrTm | TCS | stVal | ST |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | Enumeration reflecting the potential error which has happened at the latest Schedule Enabling request | enumeration | / | R | change | METEO | PVGEN_ | FSCH | SchdEnaErr | ENS | stVal | ST | ScheduleEnablingErrorKind | IEC 61850 | SGIS
SCHD_INFO | data interface |  | Current value determined by the schedule. As long as the schedule is not running the quality of the value is invalid. The unit of this data shall be the same as the unit of the data object(s) ValASG | float | / | R | change | METEO | PVGEN_ | FSCH | ValMV | MV | mag | MX |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | (controllable) Operating with value true initiates enable transition request according to the state diagram; operating with value false is ignored. The change of its status value is a local issue. | boolean | / | R/W | change | METEO | PVGEN_ | FSCH | EnaReq | SPC | ctlVal |  |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | (controllable) Operating with value true initiates disable transition request according to the state diagram; operating with value false is ignored. The change of its status value is a local issue. | boolean | / | R/W | change | METEO | PVGEN_ | FSCH | DsaReq | SPC | ctlVal |  |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | The priority relation of this schedule (0..n) with higher numbers superseding lower numbers. Shall be a positive value. If missing the default is zero. | unsigned integer | / | R/W | change | METEO | PVGEN_ | FSCH | SchdPrio | ING | setVal | SP |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | The number of schedule entries that are valid out of the instantiated ValASG, ValING, ValSPG or ValENG. NumEntr shall be > 0. NumEntr is <= number of instantiated Val[ASG¦ING¦SPG¦ENG]'s | unsigned integer | / | R/W | change | METEO | PVGEN_ | FSCH | NumEntr | ING | setVal | SP |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | The schedule interval duration in time entities as specified in the unit. The SIUnit is mandatory in this data object. The total duration of a schedule shall be (NumEntr x SchdIntv). | unsigned integer | s | R/W | change | METEO | PVGEN_ | FSCH | SchdIntv | ING | setVal | SP |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | The ASG scheduled values (current value output as MV). Multiple entries should be possible. | float | / | R/W | change | METEO | PVGEN_ | FSCH | ValASG | ASG | setMag | SP |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | Start time of the schedule in UTC time. | timestamp | / | R/W | change | METEO | PVGEN_ | FSCH | StrTm | TSG | setTm | SP |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | If true, the change of the schedule to the running and activated state is triggered by an external event and not by the start time. The external event is referenced through 'InSyn'. | boolean | / | R/W | change | METEO | PVGEN_ | FSCH | EvtTrg | SPG | setVal | SP |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | Object reference of the external trigger if the schedule is triggered by an event. | objectReference | / | R/W | change | METEO | PVGEN_ | FSCH | InSyn | ORG | setSrcRef | SP |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | If true, once terminated or disabled, the schedule will change to the validated state, otherwise it will change to the not ready state. | boolean | / | R/W | change | METEO | PVGEN_ | FSCH | SchdReuse | SPG | setVal | SP |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | Object reference of data object bound to the input n. | objectReference | / | R/W | change | METEO | PVGEN_ | FSCH | InRef | ORG | setSrcRef | SP |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | PV active power forecast schedule controller manager | character | / | R | Initial | METEO | PVGEN_ | FSCC | NamPlt | LPL | vendor | DC |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | PV active power forecast schedule controller revision | character | / | R | Initial | METEO | PVGEN_ | FSCC | NamPlt | LPL | swRev | DC |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | PV active power forecast schedule controller description | character | / | R | Initial | METEO | PVGEN_ | FSCC | NamPlt | LPL | d | DC |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | A placeholder for later use | character | / | R | Initial | METEO | PVGEN_ | FSCC | NamPlt | LPL | configRev | DC |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | Indication of which schedule is active as an object reference. As long as no schedule is active the quality of the value is invalid. The active schedule is selected by the schedule controller within the running schedules based on the priority of the running schedules. | objectReference | / | R | change | METEO | PVGEN_ | FSCC | ActSchdRef | ORS | stVal | ST |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | Current value determined by the schedule. As long as the schedule is not running the quality of the value shall be set to invalid. The unit of this data shall be the same as the unit of the data object(s) FSCH.ValASG. | float | W | R | change | METEO | PVGEN_ | FSCC | ValMV | MV | mag | MX |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | Object reference to the entity controlled by the schedule. | objectReference | / | R/W | change | METEO | PVGEN_ | FSCC | CtlEnt | ORG | setSrcRef | SP |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | Object reference of schedule n (an LN reference to the LN of class FSCH). | objectReference | / | R/W | change | METEO | PVGEN_ | FSCC | Schd | ORG | setSrcRef | SP |  | IEC 61850 | SGIS
SCHD_INFO | data interface |  | Object reference of data object bound to the input n. | objectReference | / | R/W | change | METEO | PVGEN_ | FSCC | InRef | ORG | setSrcRef | SP |  | IEC 61850 | SGIS

## Lists of Values
Paramete categories |  | Object | Commonly used data types |  | Read/Write |  | Data transmission |  | Origin of the parameter |  | Contributor
HW_META | system hardware meta-data | PV-Inverter | integer | an integer value | R/W | read and write | Initial | only by initialization | sunspec specification | Parameter in the Sunspec specification | THU
SW_META | system software meta-data | PV-panel | unsigned integer | non-negative integer values | R | read only | change | upon value/quality change | WP6 | Inputs from T6.1 and T6.2 | FIB
GEO_REF | geographical reference | Electrical storage | float | an float value | W | write only | integrity | regular query (e.g. using reports) | IEC 61850 | Parameter provided by IEC 61850 standards | ING
MEAS_VAL | measured values | E-Charging | enumeration | a list of possible values |  |  | change & integrity | both on data update and in cycle | IEEE 1547.1 | IEEE 1547.1 | MLS
STAT_INFO | device status information | Load | character | string, raw character bytes |  |  |  |  | DNP3 | Parameter provided by DNP3 standard | SGIS
CTRL_PARA | control parameters | Communication Unit | boolean | yes/no |  |  |  |  | experience | working experience | Others X
SCHD_INFO | schedule | PCC | timestamp | Reserve1 |  |  |  |  | registry | documentation of registration platforms | Others Y
OWNER_INFO | system owner information | HEMS | objectReference | Reserve2 |  |  |  |  | DSO | parameter required by DSO
FLEX_INFO | flexibility information | PV Array | Curve | Reserve3 |  |  |  |  | market | parameter required by market partner
MKT_IF | market interfaces | Tracking system | xy | Reserve4 |  |  |  |  | others | other technical specicifations
OP_FUNC | operational functions | data interface | xy | Reserve5 |  |  |  |  | thucls | parameters in existing THU data models thucls
METEO_INFO | meteorological monitoring | ECP | [6 empty] | xy
HEMS_INFO | home energy mgmt system control | [7 empty] | xy
AUTH_INFO | security/authentification information
DATA_IF | external data interface
SETTING | Technical rating & environmental setting

## IEC 61850 short description
IEC 61850 definitions
LD | Logical Device
LN | Logical Node
DO | Data Object
DA | Data Attribute
CDC | Common Data Class
FC | Functional Constraint
DS | Data Set
RCB | Report Control Block

## IEC 61850 LNs
This is a collection of IEC 61850 Logical Nodes (LN) related to DER integration.
More LN may be added to the list, rows in bold are vital for the implementation in T6.3.
Function | description | LNs | relavente Standard
Switchgear operation | functions for the control and monitoring of breakers and disconnect devices | XCBR, XSWI, CSWI | 61850-7-4
protection | functions required to protect the electrical equipment and personnel in case of a malfunction | PTOC, PTOV, PTTR, PHIZ | 61850-7-4
Measuring and metering | functions required to obtain electrical measurements like voltage and current. | MMXU/MMXN, MMTR/MMTN, MMDC | 61850-7-4
DC to AC conversion | functions for the control and monitoring of the inverter | DINV & SINV | 61850-7-420
Array operation | functions to maximize the power output of the array | DPVC, DTRC | 61850-7-420
Islanding | functions required to synchronize the PV system operation with the power system | DHVT, DLVT, DHFT, DLFT, RSYN | 61850-7-4, 61850-7-420
Energy storage | functions required to store excess energy produced by the system | DSTO, DBAT, SBAT | 61850-7-420
Meteorological monitoring | functions required to obtain meteorological measurement like solar irradiation and ambient temperature | MMET, STMP | 61850-7-4
Schedule | Schedule and schedule controller | FSCH, FSCC | 61850-7-4
Grid coupling | (Virtual) Grid coupling point | DECP, DPCC, DVER | 61850-7-420
Home Energy Management | interaction with existing home energy management system | DPMC | 61850-7-420
Distributed Energy System | Distributed Loads and Generation | DLOD, DGEN | 61850-7-420
Economic dispatch | Economic dispatch parameters and information | DCCT, DSCT | 61850-7-420
CLS
DPCC
LLN0
LPHD
PCC
MMXU
LLN0
MMTR
PV
STO
LLN0
LLN0
DECP
MMXU
MMTR
DGEN
DINV
DCCT
DSCT
MMXU
MMTR
FSCH
FSCC
LLN0
DECP
DSTO
DCCT
DSCT
MMXU
MMTR
FSCH
FSCC
LLN0
DECP
DLOD
DCCT
DSCT
MMXU
MMTR
LOAD
METEO
LLN0
LPHD
MMET
FSCH
FSCC

## data_model_config
Category | Object | description | type | unit | R/W | transmission | LD | Prefix | LN | DO | CDC | DA | FC | EnumKInd
OWNER_INFO | Owner | Prosumer UUID | character | / | R | Initial
OWNER_INFO | Owner | responsible DSO | character | / | R | change
OWNER_INFO | Owner | responsible MPO | character | / | R | change
OWNER_INFO | Owner | postal code | character | / | R | Initial
GEO_REF | Owner | Prosumer Label | character | / | R | Initial
GEO_REF | Owner | location | character | / | R | Initial
GEO_REF | Owner | geo longtitude | float | / | R | Initial
GEO_REF | Owner | geo latitude | float | / | R | Initial
MKT_IF | Owner | list of market partners | character | / | R | change
MKT_IF | Owner | metering number | character | / | R | change
HW_META | Communication Unit | CLS-gateway name | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | name | DC
HW_META | Communication Unit | CLS-gateway hardware vendor | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | vendor | DC
HW_META | Communication Unit | CLS-gateway hardware model | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | model | DC
HW_META | Communication Unit | CLS-gateway hardware serial number | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | serNum | DC
SW_META | Communication Unit | CLS-gateway software revision | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | swRev | DC
HW_META | Communication Unit | CLS-gateway location | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | location | DC
HW_META | Communication Unit | CLS-gateway longitude, WGS84 coordinates | float | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | longitude | DC
HW_META | Communication Unit | CLS-gateway altitude, WGS84 coordinates | float | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | altitude | DC
HW_META | Communication Unit | CLS-gateway owner | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | owner | DC
HW_META | Communication Unit | CLS-gateway connected electrical power system | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | ePSName | DC
HW_META | Communication Unit | CLS-gateway primary operator | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | primeOper | DC
HW_META | Communication Unit | CLS-gateway secondary operator | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | secondOper | DC
STAT_INFO | Communication Unit | CLS-gateway hardware reversion | character | / | R | Change | CLS | Hardware_ | LPHD | PhyNam | DPL | hwRev | DC
STAT_INFO | Communication Unit | CLS-gateway hardware UUID | character | / | R | Initial | CLS | Hardware_ | LPHD | PhyNam | DPL | mRID | DC
STAT_INFO | Communication Unit | CLS-gateway hardware description | character | / | R | change | CLS | Hardware_ | LPHD | PhyNam | DPL | d | DC
STAT_INFO | Communication Unit | CLS-gateway hardware failure description | character | / | R | Change | CLS | Hardware_ | LPHD | Beh | ENS | d | DC
STAT_INFO | Communication Unit | CLS-application platform name | character | / | R | Initial | CLS | Platform_ | LPHD | PhyNam | DPL | name | DC
STAT_INFO | Communication Unit | CLS-application platform vendor | character | / | R | Initial | CLS | Platform_ | LPHD | PhyNam | DPL | vendor | DC
STAT_INFO | Communication Unit | CLS-application platform software revision | character | / | R | Initial | CLS | Platform_ | LPHD | PhyNam | DPL | swRev | DC
STAT_INFO | Communication Unit | CLS-application platform hardware reversion | character | / | R | Change | CLS | Platform_ | LPHD | PhyNam | DPL | hwRev | DC
STAT_INFO | Communication Unit | CLS-application platform failure description | character | / | R | Change | CLS | Platform_ | LPHD | Beh | ENS | d | DC
SW_META | Communication Unit | CLS-software plug-in application provider | character | / | R | Initial | CLS |  | LLN0 | NamPlt | LPL | vendor | DC
SW_META | Communication Unit | CLS-software application version | character | / | R | Initial | CLS |  | LLN0 | NamPlt | LPL | swRev | DC
SW_META | Communication Unit | CLS-software application description | character | / | R | Initial | CLS |  | LLN0 | NamPlt | LPL | d | DC
SW_META | Communication Unit | A placeholder for later use | character | / | R | Initial | CLS |  | LLN0 | NamPlt | LPL | configRev | DC
STAT_INFO | Communication Unit | CLS-software failure description | character | / | R | Change | CLS |  | LLN0 | Beh | ENS | d | DC
OP_FUNC | Communication Unit | local controller lock | boolean | / | R | Change | CLS
STAT_INFO | Communication Unit | CLS connectivity (defined by the IEC61850 client) | float | % | R/W | Change | CLS
SW_META | PCC | Name plate of the logical node | character | / | R | Initial | PCC |  | LLN0 | NamPlt | LPL | vendor | DC
SW_META | PCC | Name plate of the logical node | character | / | R | Initial | PCC |  | LLN0 | NamPlt | LPL | swRev | DC
SW_META | PCC | Number of PV Inverters (represent integer by string) | character | / | R | Initial | PCC |  | LLN0 | NamPlt | LPL | d | DC
SW_META | PCC | A placeholder for later use | character | / | R | Initial | PCC |  | LLN0 | NamPlt | LPL | configRev | DC
STAT_INFO | PCC | PCC data service failure description | character | / | R | Change | PCC |  | LLN0 | Beh | ENS | d | DC
HW_META | PCC | PCC service provider | character | / | R | Initial | PCC |  | DPCC | NamPlt | LPL | vendor | DC
HW_META | PCC | PCC service software version | character | / | R | Initial | PCC |  | DPCC | NamPlt | LPL | swRev | DC
HW_META | PCC | PCC service description | character | / | R | Initial | PCC |  | DPCC | NamPlt | LPL | d | DC
HW_META | PCC | A placeholder for later use | character | / | R | Initial | PCC |  | DPCC | NamPlt | LPL | configRev | DC
CTRL_PARA | PCC | Identification of the ECP from the Area Electric Power System | character | / | R | Initial | PCC |  | DPCC | AreaEpsEcpId | VSG | setVal | SP
CTRL_PARA | PCC | Maximum active power at the PCC for area EPS | float | W | R | Initial | PCC |  | DPCC | AreaEpsWMax | ASG | setMag | SP
HW_META | PCC | Type of circuit phases | enumeration | / | R | Initial | PCC |  | DPCC | PhsConnTyp | ENS | stVal | ST | PhaseKind
SETTING | PCC | Default reference voltage for functions using voltage at this ECP as input. It may be overridden by Vref setpoints in specific operational functions. | float | V | R/W | change | PCC |  | DPCC | VRef | ASG | setMag | SP
SETTING | PCC | Percent of VRef to use in calculating the voltage to use in operational function calculations | float | % | R/W | change | PCC |  | DPCC | VRefPct | ASG | setMag | SP
SETTING | PCC | Electrical active power rating at ECP | float | W | R/W | change | PCC |  | DPCC | WRtg | ASG | setMag | SP
SETTING | PCC | Reactive power rating at ECP | float | Var | R/W | change | PCC |  | DPCC | VArRtg | ASG | setMag | SP
SETTING | PCC | Apparent power rating at ECP | float | VA | R/W | change | PCC |  | DPCC | VARtg | ASG | setMag | SP
SETTING | PCC | Voltage rating at ECP | float | V | R/W | change | PCC |  | DPCC | VRtg | ASG | setMag | SP
SETTING | PCC | Nominal frequency at ECP | float | Hz | R/W | change | PCC |  | DPCC | HzNom | ASG | setMag | SP
SETTING | PCC | Rated maximum voltage | float | V | R/W | change | PCC |  | DPCC | VMax | ASG | setMag | SP
SETTING | PCC | Rated minimum voltage | float | V | R/W | change | PCC |  | DPCC | Vmin | ASG | setMag | SP
CTRL_PARA | PCC | Identity of electrical reference point as a Visible String | character | / | R/W | change | PCC |  | DPCC | ElcRefId | VSG | setVal | SP
CTRL_PARA | PCC | Determine self-consumption; Indication whether the active power from the DER referencing this ECP is included in the measurements coming from the ECP. This is important for managing Generation and Load Following, as well as Peak Power Limiting functions. | boolean | / | R | change | PCC |  | DPCC | DERMsIncl | SPG | setVal | SP
HW_META | PCC | measuring unit vendor | character | / | R | Initial | PCC |  | MMXU | NamPlt | LPL | vendor | DC
HW_META | PCC | measuring unit software version | character | / | R | Initial | PCC |  | MMXU | NamPlt | LPL | swRev | DC
HW_META | PCC | measuring unit description | character | / | R | Initial | PCC |  | MMXU | NamPlt | LPL | d | DC
HW_META | PCC | A placeholder for later use | character | / | R | Initial | PCC |  | MMXU | NamPlt | LPL | configRev | DC
STAT_INFO | PCC | status of the power vector expressed through one of the 9 zones of the PQ diagram quadrant, based on the signing conventions set with PFSign and PFExt. | enumeration | / | R | change | PCC |  | MMXU | PQSt | ENS | stVal | ST | QuadrantRunningStateKind
MEAS_VAL | PCC | total active power measurement | float | W | R | change & integrity | PCC |  | MMXU | TotW | MV | mag | MX
MEAS_VAL | PCC | total reactive power measurement | float | Var | R | change & integrity | PCC |  | MMXU | TotVAr | MV | mag | MX
MEAS_VAL | PCC | total apparent power measurement | float | VA | R | change & integrity | PCC |  | MMXU | TotVA | MV | mag | MX
MEAS_VAL | PCC | ratio of the absolute active power to the apparent power | float | / | R | change & integrity | PCC |  | MMXU | TotPF | MV | mag | MX
MEAS_VAL | PCC | frequency | float | Hz | R | change & integrity | PCC |  | MMXU | Hz | MV | mag | MX
MEAS_VAL | PCC | Phase to phase voltages. | float | V | R | change & integrity | PCC |  | MMXU | PPV | DEL | phsAB/BC/CA.cVal.mag | MX
MEAS_VAL | PCC | Phase to neutral voltages. | float | V | R | change & integrity | PCC |  | MMXU | PNV | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PCC | Phase to ground (line) voltages. | float | V | R | change & integrity | PCC |  | MMXU | PhV | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PCC | Phase to ground/phase to neutral three phase currents. | float | A | R | change & integrity | PCC |  | MMXU | A | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PCC | Phase to ground/phase to neutral real powers P. | float | W | R | change & integrity | PCC |  | MMXU | W | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PCC | Phase to ground/phase to neutral reactive powers Q. | float | Var | R | change & integrity | PCC |  | MMXU | VAr | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PCC | Phase to ground/phase to neutral apparent powers S. | float | VA | R | change & integrity | PCC |  | MMXU | VA | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PCC | Phase to ground/phase to neutral signed power factors. | float | / | R | change & integrity | PCC |  | MMXU | PF | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PCC | Phase to ground/phase to neutral impedances in a three-phase system. | float | ohm | R | change & integrity | PCC |  | MMXU | Z | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PCC | Rate of change of frequency | float | Hz/s | R | change & integrity | PCC |  | MMXU | HzRte | MV | mag | MX
MEAS_VAL | PCC | Arithmetic average of the magnitude of current of the 3 phases: average(Ia,Ib,Ic). | float | A | R | change & integrity | PCC |  | MMXU | AvAPhs | MV | mag | MX
MEAS_VAL | PCC | Arithmetic average of the magnitude of phase to phase voltage of the 3 phases: average(PPVa, PPVb, PPVc). | float | V | R | change & integrity | PCC |  | MMXU | AvPPVPhs | MV | mag | MX
MEAS_VAL | PCC | Arithmetic average of the magnitude of phase to reference voltage of the 3 phases: average(PhVa, PhVb, PhVc). | float | V | R | change & integrity | PCC |  | MMXU | AvPhVPhs | MV | mag | MX
MEAS_VAL | PCC | Arithmetic average of the magnitude of active power of the 3 phases: average(Wa, Wb, Wc). | float | W | R | change & integrity | PCC |  | MMXU | AvWPhs | MV | mag | MX
MEAS_VAL | PCC | Arithmetic average of the magnitude of apparent power of the 3 phases: average(VAa, VAb, VAc). | float | Var | R | change & integrity | PCC |  | MMXU | AvVAPhs | MV | mag | MX
MEAS_VAL | PCC | Arithmetic average of the magnitude of reactive power of the 3 phases: average(VAra, VArb, VArc). | float | VA | R | change & integrity | PCC |  | MMXU | AvVArPhs | MV | mag | MX
MEAS_VAL | PCC | Arithmetic average of the magnitude of power factor of the 3 phases: average(PFa, PFb, PFc). | float | / | R | change & integrity | PCC |  | MMXU | AvPFPhs | MV | mag | MX
MEAS_VAL | PCC | Arithmetic average of the magnitude of impedance of the 3 phases: average(Za, Zb, Zc). | float | ohm | R | change & integrity | PCC |  | MMXU | AvZPhs | MV | mag | MX
MEAS_VAL | PCC | meter vendor | character | / | R | Initial | PCC |  | MMTR | NamPlt | LPL | vendor | DC
MEAS_VAL | PCC | meter software version | character | / | R | Initial | PCC |  | MMTR | NamPlt | LPL | swRev | DC
MEAS_VAL | PCC | meter description | character | / | R | Initial | PCC |  | MMTR | NamPlt | LPL | d | DC
MEAS_VAL | PCC | meter configuration revision | character | / | R | Initial | PCC |  | MMTR | NamPlt | LPL | configRev | DC
MEAS_VAL | PCC | Net apparent energy since last reset. | integer | VAh | R | change & integrity | PCC |  | MMTR | TotVAh | BCR | actVal | ST
MEAS_VAL | PCC | Net real energy since last reset. | integer | Wh | R | change & integrity | PCC |  | MMTR | TotWh | BCR | actVal | ST
MEAS_VAL | PCC | Net reactive energy since last reset. | integer | VArh | R | change & integrity | PCC |  | MMTR | TotVArh | BCR | actVal | ST
MEAS_VAL | PCC | Real energy supply (default direction: towards busbar). | integer | Wh | R | change & integrity | PCC |  | MMTR | SupWh | BCR | actVal | ST
MEAS_VAL | PCC | Reactive energy supply (default direction: towards busbar). | integer | VArh | R | change & integrity | PCC |  | MMTR | SupVArh | BCR | actVal | ST
MEAS_VAL | PCC | Real energy demand (direction: from busbar). | integer | Wh | R | change & integrity | PCC |  | MMTR | DmdWh | BCR | actVal | ST
MEAS_VAL | PCC | Reactive energy demand (direction: from busbar). | integer | VArh | R | change & integrity | PCC |  | MMTR | DmdVArh | BCR | actVal | ST
HW_META | PV-panel | Panel UUID | xy | / |  | Initial
HW_META | PV-panel | Type panel | xy | / |  | Initial
HW_META | PV-panel | Panel azimut angle | xy | / |  | Initial
HW_META | PV-panel | Panel elevation angle | xy | / |  | Initial
HW_META | PV-panel | panel power | xy |  |  | Initial
HW_META | PV-panel | Device nameplate (e.g. JKM530M-72HL4-BDVP) (DPVM, data object name: EEName) - OPTIONAL | character |  | R | Initial
HW_META | PV-panel | Latitude (six decimal places) (DPVM, data object name: EEName) - MUST | float |  | R | Initial
HW_META | PV-panel | Longitude (six decimal places) (DPMV, data object name: EEName) - MUST | float |  | R | Initial
HW_META | PV-panel | Bifaciality factor (between 0 and 1, the ratio of rear efficiency in relation to the front efficiency) - MUST (if bifacial modules are used) | float |  | R | Initial
HW_META | PV-panel | Module rated power at watts peak STC (DPVM, data object name: MdulWRtg) - MUST | float | Wp | R | Initial
HW_META | PV-panel | Technology: e.g. monoSi, polySi, CdTe, mtHIT (Heterojunction with Intrinsic Thin layer solar cell), …OPTIONAL | character |  | R | Initial
HW_META | PV-panel | Length of a PV module - OPTIONAL | float | m | R | Initial
HW_META | PV-panel | Width of a PV module - OPTIONAL | float | m | R | Initial
HW_META | PV-panel | Thickness of a PV module - OPTIONAL | float | m | R | Initial
HW_META | PV-panel | Number of cells in series - OPTIONAL | unsigned integer |  | R | Initial
HW_META | PV-panel | Number of cells in parallel - OPTIONAL | unsigned integer |  | R | Initial
HW_META | PV-panel | Number of bypass diode - OPTIONAL | unsigned integer |  | R | Initial
HW_META | PV-panel | Cell arrea - OPTIONAL | float | m2 | R | Initial
HW_META | PV-panel | Nominal operating cell temperature (NOCT) - OPTIONAL | float | °C | R | Initial
HW_META | PV-panel | Module open circuit voltage (Voc at STC) (DPVM, data object name: MdulOcV) - OPTIONAL | float | V | R | Initial
HW_META | PV-panel | Module short circuit current (Isc at STC) (DPVM, data object name: MdulScA) - OPTIONAL | float | A | R | Initial
HW_META | PV-panel | Shunt resistance of a PV module - OPTIONAL | float | Ohm | R | Initial
HW_META | PV-panel | Series resistance of a PV module - OPTIONAL | float | Ohm | R | Initial
HW_META | PV-panel | Module current/temperature derate as percent of degrees above 25 ºC (DPVM, data object name: MdulATmpDrt) - OPTIONAL | float | %/°C | R | Initial
HW_META | PV-panel | Number of bypass diodes - OPTIONAL | unsigned integer |  | R | Initial
HW_META | PV-panel | Module age derate as percent over time (DPVM, data object name: MdulDrtPct) - OPTIONAL | float | %/year | R | Initial
HW_META | PV-panel | Diode ideality (quality) factor - OPTIONAL | float |  | R | Initial
SW_META | ECP | Name plate of the logical node | character | / | R | Initial | PV |  | LLN0 | NamPlt | LPL | vendor | DC
SW_META | ECP | Name plate of the logical node | character | / | R | Initial | PV |  | LLN0 | NamPlt | LPL | swRev | DC
SW_META | ECP | Name plate of the logical node | character | / | R | Initial | PV |  | LLN0 | NamPlt | LPL | d | DC
SW_META | ECP | A placeholder for later use | character | / | R | Initial | PV |  | LLN0 | NamPlt | LPL | configRev | DC
STAT_INFO | ECP | ECP data service failure description | character | / | R | Change | PV |  | LLN0 | Beh | ENS | d | DC
SW_META | ECP | ECP service provider | character | / | R | Initial | PV |  | DECP | NamPlt | LPL | vendor | DC
SW_META | ECP | ECP service software version | character | / | R | Initial | PV |  | DECP | NamPlt | LPL | swRev | DC
SW_META | ECP | ECP service description | character | / | R | Initial | PV |  | DECP | NamPlt | LPL | d | DC
SW_META | ECP | A placeholder for later use | character | / | R | Initial | PV |  | DECP | NamPlt | LPL | configRev | DC
STAT_INFO | ECP | Type of circuit phases | enumeration | / | R | Initial | PV |  | DECP | PhsConnTyp | ENS | stVal | ST | PhaseKind
SETTING | ECP | Default reference voltage for functions using voltage at this ECP as input | float | V | R/W | change | PV |  | DECP | VRef | ASG | setMag | SP
SETTING | ECP | Percent of VRef to use in calculating the voltage to use in operational function calculations | float | % | R/W | change | PV |  | DECP | VRefPct | ASG | setMag | SP
SETTING | ECP | Electrical active power rating at ECP | float | W | R/W | change | PV |  | DECP | WRtg | ASG | setMag | SP
SETTING | ECP | Reactive power rating at ECP | float | Var | R/W | change | PV |  | DECP | VArRtg | ASG | setMag | SP
SETTING | ECP | Apparent power rating at ECP | float | VA | R/W | change | PV |  | DECP | VARtg | ASG | setMag | SP
SETTING | ECP | Voltage rating at ECP | float | V | R/W | change | PV |  | DECP | VRtg | ASG | setMag | SP
SETTING | ECP | Nominal frequency at ECP | float | Hz | R/W | change | PV |  | DECP | HzNom | ASG | setMag | SP
SETTING | ECP | Rated maximum voltage | float | V | R/W | change | PV |  | DECP | VMax | ASG | setMag | SP
SETTING | ECP | Rated minimum voltage | float | V | R/W | change | PV |  | DECP | Vmin | ASG | setMag | SP
CTRL_PARA | ECP | Identity of electrical reference point as a Visible String | character | / | R/W | change | PV |  | DECP | ElcRefId | VSG | setVal | SP
CTRL_PARA | ECP | Indication whether the active power from the DER referencing this ECP is included in the measurements coming from the ECP. This is important for managing Generation and Load Following, as well as Peak Power Limiting functions. | boolean | / | R | change | PV |  | DECP | DERMsIncl | SPG | setVal | SP
CTRL_PARA | ECP | Reference to electrical measurement/calculation function, typically MMXU, MMXN or MMDC, MMTR LN instances | objectReference | / | R/W | change | PV |  | DECP | ElcMsRef | ORG | setSrcRef | SP
HW_META | PV-Inverter | PV inverter name | character | / | R | Initial | PV |  | DGEN | EEName | DPL | name | DC
HW_META | PV-Inverter | PV inverter hardware vendor | character | / | R | Initial | PV |  | DGEN | EEName | DPL | vendor | DC
HW_META | PV-Inverter | PV inverter hardware model | character | / | R | Initial | PV |  | DGEN | EEName | DPL | model | DC
HW_META | PV-Inverter | PV inverter hardware serial number | character | / | R | Initial | PV |  | DGEN | EEName | DPL | serNum | DC
SW_META | PV-Inverter | PV inverter software revision | character | / | R | Initial | PV |  | DGEN | EEName | DPL | swRev | DC
HW_META | PV-Inverter | PV inverter owner | character | / | R | Initial | PV |  | DGEN | EEName | DPL | owner | DC
HW_META | PV-Inverter | PV inverter connected electrical power system | character | / | R | Initial | PV |  | DGEN | EEName | DPL | ePSName | DC
HW_META | PV-Inverter | PV inverter primary operator | character | / | R | Initial | PV |  | DGEN | EEName | DPL | primeOper | DC
HW_META | PV-Inverter | PV inverter secondary operator | character | / | R | Initial | PV |  | DGEN | EEName | DPL | secondOper | DC
STAT_INFO | PV-Inverter | PV inverter hardware reversion | character | / | R | Change | PV |  | DGEN | EEName | DPL | hwRev | DC
STAT_INFO | PV-Inverter | PV inverter hardware UUID | character | / | R | Initial | PV |  | DGEN | EEName | DPL | mRID | DC
STAT_INFO | PV-Inverter | PV inverter hardware description | character | / | R | Change | PV |  | DGEN | EEName | DPL | d | DC
STAT_INFO | PV-Inverter | Name plate of the logical node | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | vendor | DC
STAT_INFO | PV-Inverter | Name plate of the logical node | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | swRev | DC
STAT_INFO | PV-Inverter | Name plate of the logical node | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | d | DC
STAT_INFO | PV-Inverter | A placeholder for later use | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | configRev | DC
STAT_INFO | PV-Inverter | PV inverter hardware failure description | character | / | R | Change | PV |  | DGEN | Beh | ENS | d | DC
STAT_INFO | PV-Inverter | Current state of operation of the distributed energy resource. | enumeration | / | R | Change | PV |  | DGEN | DEROpSt | ENS | stVal | ST | DERStateKind
STAT_INFO | PV-Inverter | Operation time of the external (electrical, mechanical or communication) equipment since start of the operation. | integer | h | R | Change | PV |  | DGEN | OpTmh | INS | stVal | ST
STAT_INFO | PV-Inverter | State of external (electrical, mechanical or communication) equipment to which the logical node is associated. | enumeration | / | R | Change | PV |  | DGEN | EEHealth | ENS | stVal | ST | HealthKind
FLEX_INFO | PV-Inverter | The calculation of the maximum power that the generator could output, based on constraining environmental conditions (e.g. solar insolation or wind speed or constraints from heat or vibrations). The delta between this calculation and the actual power being output indicates how much additional power could be output. | float | / | R | change & integrity | PV |  | DGEN | CnstWMax | MV | mag | MX
MEAS_VAL | PV-Inverter | Total energy generated | float | Wh | R | change & integrity | PV |  | DGEN | GnEnTot | MV | mag | MX
MEAS_VAL | PV-Inverter | Energy generated during the period since last reset | float | Wh | R | change & integrity | PV |  | DGEN | GnEnPer | MV | mag | MX
FLEX_INFO | PV-Inverter | The total amount of reactive power available for absorbing even if possibly impacting active power output (the use of this DO is mutually exclusive with the use of VArTot) | float | VAr | R | change & integrity | PV |  | DGEN | AvarTot | MV | mag | MX
FLEX_INFO | PV-Inverter | The total amount of reactive power available for injecting even if possibly impacting active power output (the use of this DO is mutually exclusive with the use of VArTot) | float | VAr | R | change & integrity | PV |  | DGEN | IvarTot | MV | mag | MX
FLEX_INFO | PV-Inverter | The amount of reactive power available for absorbing without impacting active power output (the use of this DO is mutually exclusive with the use of VArAvl) | float | VAr | R | change & integrity | PV |  | DGEN | AvarAvl | MV | mag | MX
FLEX_INFO | PV-Inverter | The amount of reactive power available for injecting without impacting active power output (the use of this DO is mutually exclusive with the use of VArAvl) | float | VAr | R | change & integrity | PV |  | DGEN | IvarAvl | MV | mag | MX
FLEX_INFO | PV-Inverter | Actual self service energy used | float | Wh | R | change & integrity | PV |  | DGEN | SelfSvcWh | MV | mag | MX
MEAS_VAL | PV-Inverter | Actual percentage of apparent power output based on VAMax | float | % | R | change & integrity | PV |  | DGEN | VAPct | MV | mag | MX
FLEX_INFO | PV-Inverter | Available capability (measured or calculated) for increasing active output, including increasing generation of active power, even if currently consuming power. | float | W | R | change & integrity | PV |  | DGEN | AvlUpW | MV | mag | MX
FLEX_INFO | PV-Inverter | Available capability (measured or calculated) for decreasing active power, including increasing the consumption of active power, even if currently generating power. | float | W | R | change & integrity | PV |  | DGEN | AvlDnW | MV | mag | MX
STAT_INFO | PV-Inverter | The number of times that the DER unit has been turned on or returned to service: count of "DER unit on" times, since the last time the counter was reset | unsigned integer | / | R | change | PV |  | DGEN | GnOnCnt | INC | stVal | ST
STAT_INFO | PV-Inverter | Count of total number of starts | unsigned integer | / | R | change | PV |  | DGEN | TotStrCnt | INC | stVal | ST
STAT_INFO | PV-Inverter | Count of starts in period since reset | unsigned integer | / | R | change | PV |  | DGEN | PerStrCnt | INC | stVal | ST
STAT_INFO | PV-Inverter | Total time DER unit has operated – resettable: accumulated time since the last time the time was reset | integer | s | R | change | PV |  | DGEN | OpTms | INC | stVal | ST
CTRL_PARA | PV-Inverter | (controllable) Operating with the value expressed in ctlVal (selected among the list specified in DERStateControlKind) initiates the appropriate transition request. The reading of its attribute stVal is meaningless. The resulting state of the DER shall be observed in the DEROpSt DO. | enumeration | / | W | change | PV |  | DGEN | DEROpStCtl | ENC | ctlVal |  | DERStateTransitionKind
CTRL_PARA | PV-Inverter | Active power setpoint | float | W | W | change | PV |  | DGEN | WSpt | APC | ctlVal
CTRL_PARA | PV-Inverter | Requested active power setpoint | float | W | R | change & integrity | PV |  | DGEN | WSpt | APC | mxVal | MX
CTRL_PARA | PV-Inverter | Reactive power setpoint | float | VAr | W | change | PV |  | DGEN | VArSpt | APC | ctlVal
CTRL_PARA | PV-Inverter | Requested reactive power setpoint | float | VAr | R | change & integrity | PV |  | DGEN | VArSpt | APC | mxVal | MX
STAT_INFO | PV-Inverter | (controllable) Operations count, can be reset to a value different than 0. | integer | / | R/W | change | PV |  | DGEN | OpCntRs | INC | stVal | ST
SETTING | PV-Inverter | Value of power factor defined by a network operator - MUST. DGEN defines over-/under-excited power factor, could these be used? | float | / | R | change
SETTING | PV-Inverter | Nameplate maximum active generation power rating at unity power factor | float | W | R/W | change | PV |  | DGEN | WMaxRtg | ASG | setMag | SP
SETTING | PV-Inverter | Nameplate maximum apparent power generation rating | float | VA | R/W | change | PV |  | DGEN | VAMaxRtg | ASG | setMag | SP
SETTING | PV-Inverter | Rating for maximum absorbing reactive power | float | VAr | R/W | change | PV |  | DGEN | AvarMaxRtg | ASG | setMag | SP
SETTING | PV-Inverter | Rating for maximum supply (injection) reactive power | float | VAr | R/W | change | PV |  | DGEN | IvarMaxRtg | ASG | setMag | SP
SETTING | PV-Inverter | Maximum current rating under nominal voltage under nominal power factor | float | A | R/W | change | PV |  | DGEN | AMaxRtg | ASG | setMag | SP
SETTING | PV-Inverter | Maximum voltage rating | float | V | R/W | change | PV |  | DGEN | VMaxRtg | ASG | setMag | SP
SETTING | PV-Inverter | Minimum voltage rating | float | V | R/W | change | PV |  | DGEN | VMinRtg | ASG | setMag | SP
SETTING | PV-Inverter | Maximum generation active power ramp up rating | float | W | R/W | change | PV |  | DGEN | WRpuMaxRtg | ASG | setMag | SP
SETTING | PV-Inverter | Maximum generation active power ramp down rating | float | W | R/W | change | PV |  | DGEN | WRpdMaxRtg | ASG | setMag | SP
SETTING | PV-Inverter | Max rated active power (WMaxRtg) which may result from controllable resource, .i.e whose level can be potentially controlled/set under the request of an entity external to the given DER. | float | W | R/W | change | PV |  | DGEN | CtbWMaxRtg | ASG | setMag | SP
SETTING | PV-Inverter | Max rated reactive power VArMaxRtg, which may result from controllable resource, .i.e whose level can be potentially controlled/set under the request of an entity external to the given DER. | float | VAr | R/W | change | PV |  | DGEN | CtbVArMaxRtg | ASG | setMag | SP
SETTING | PV-Inverter | Setting for maximum active power | float | W | R/W | change | PV |  | DGEN | WMax | ASG | setMag | SP
SETTING | PV-Inverter | Default ramp rate for changes in active power: percentage of WMax per second | float | % | R/W | change | PV |  | DGEN | WRmp | ASG | setMag | SP
SETTING | PV-Inverter | Setting for maximum absorbing reactive power (the use of this DO is mutually exclusive with the use of VArMax) | float | VAr | R/W | change | PV |  | DGEN | AvarMax | ASG | setMag | SP
SETTING | PV-Inverter | Setting for maximum supply (injection) reactive power (the use of this DO is mutually exclusive with the use of VArMax) | float | VAr | R/W | change | PV |  | DGEN | IvarMax | ASG | setMag | SP
SETTING | PV-Inverter | Setting for maximum voltage operational rating | float | V | R/W | change | PV |  | DGEN | VMax | ASG | setMag | SP
SETTING | PV-Inverter | Setting for minimum voltage operational rating | float | V | R/W | change | PV |  | DGEN | VMin | ASG | setMag | SP
SETTING | PV-Inverter | Setting for maximum operational current rating under nominal voltage under nominal power factor | float | A | R/W | change | PV |  | DGEN | AMax | ASG | setMag | SP
SETTING | PV-Inverter | Setting for maximum absorbing apparent power (the use of this DO is mutually exclusive with the use of VAMax) | float | VA | R/W | change | PV |  | DGEN | AvaMax | ASG | setMag | SP
SETTING | PV-Inverter | Setting for maximum injecting apparent power (the use of this DO is mutually exclusive with the use of VAMax) | float | VA | R/W | change | PV |  | DGEN | IvaMax | ASG | setMag | SP
SETTING | PV-Inverter | Reference for reactive power setpoints. Selects which setpoint is active. | enumeration | / | R/W | change | PV |  | DGEN | VArSptRef | ENG | setVal | SP | ReactivePowerRefParamKind
SETTING | PV-Inverter | Connection type of ECP: connection to DER (Point of Connection (PoC)), to load, within Local Electric Power System (Local EPS), Point of Common Coupling (PCC), or directly to Area EPS | enumeration | / | R/W | Initial | PV |  | DGEN | EcpConnTyp | ENG | setVal | SP | ECPConnKind
SETTING | PV-Inverter | Phase type of electrical connection of the DER | enumeration | / | R/W | change | PV |  | DGEN | PhsConnTyp | ENG | setVal | SP | PhaseKind
SETTING | PV-Inverter | Type of DER | enumeration | / | R/W | change | PV |  | DGEN | DERTyp | ENG | setVal | SP | DERUnitKind
SETTING | PV-Inverter | Maximum temperature rating | float | °C | R/W | change | PV |  | DGEN | TmpMaxRtg | ASG | setMag | SP
SETTING | PV-Inverter | Exposure to fault rates as percent of ?? | float | % | R/W | change | PV |  | DGEN | FltRtgPct | ASG | setMag | SP
SETTING | PV-Inverter | Max fault current rating | float | A | R/W | change | PV |  | DGEN | FltAMaxRtg | ASG | setMag | SP
SETTING | PV-Inverter | Max fault duration rating | float | ms | R/W | change | PV |  | DGEN | FltDurMaxTms | ASG | setMag | SP
SETTING | PV-Inverter | Selfservice nominal power | float | W | R/W | change | PV |  | DGEN | SelfWRtg | ASG | setMag | SP
SETTING | PV-Inverter | Selfservice voltage | float | V | R/W | change | PV |  | DGEN | SelfVRtg | ASG | setMag | SP
SETTING | PV-Inverter | Selfservice nominal power factor | float | / | R/W | change | PV |  | DGEN | SelfPFRtg | ASG | setMag | SP
SETTING | PV-Inverter | Sequence (direction) reversed: False = ABC, true = CBA | boolean | / | R/W | change | PV |  | DGEN | RvSeq | SPG | setVal | SP
SETTING | PV-Inverter | Efficiency at rated capacity as percent | float | / | R/W | change | PV |  | DGEN | EfcRtgPct | ASG | setMag | SP
SETTING | PV-Inverter | Rated Nominal frequency of usage of the DER | float | Hz | R/W | change | PV |  | DGEN | HzNomRtg | ASG | setMag | SP
SETTING | PV-Inverter | Rated minimal frequency of usage of the DER | float | Hz | R/W | change | PV |  | DGEN | HzMinRtg | ASG | setMag | SP
SETTING | PV-Inverter | Rated maximum frequency of usage of the DER | float | Hz | R/W | change | PV |  | DGEN | HzMaxRtg | ASG | setMag | SP
SETTING | PV-Inverter | Internal identifier of the resource within a system which is using that resource. It complements the mRID defined as part of the EEname DO. Different DERIds may be defined for different system users. | character | / | R/W | change | PV |  | DGEN | DERId | VSG | setVal | SP
STAT_INFO | PV-Inverter | Name plate of the logical node | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | vendor | DC
STAT_INFO | PV-Inverter | Name plate of the logical node | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | swRev | DC
STAT_INFO | PV-Inverter | Name plate of the logical node | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | d | DC
STAT_INFO | PV-Inverter | A placeholder for later use | character | / | R | Initial | PV |  | DGEN | NamPlt | LPL | configRev | DC
STAT_INFO | PV-Inverter | Alarm trigger status: Inverter detects loss of AC power | character | / | R | change | PV |  | DINV | InvACLosAlm | SPS | stVal | ST
STAT_INFO | PV-Inverter | Alarm trigger status: Inverter detects loss of DC power | character | / | R | change | PV |  | DINV | InvDCLosAlm | SPS | stVal | ST
STAT_INFO | PV-Inverter | Alarm trigger status: Inverter detects loss of grid power | character | / | R | change | PV |  | DINV | InvGriLosAl | SPS | stVal | ST
| PV-Inverter | Operation time of the external (electrical, mechanical or communication) equipment since start of the operation. | integer | h | R | change | PV |  | DINV | OpTmh | INS | stVal | ST
CTRL_PARA | PV-Inverter | Active power setpoint of the inverter | float | W | W | change | PV |  | DINV | WSpt | APC | ctlVal
CTRL_PARA | PV-Inverter | Requested active power setpoint of the inverter | float | W | R | change & integrity | PV |  | DINV | WSpt | APC | mxVal | MX
CTRL_PARA | PV-Inverter | Reactive power setpoint of the inverter | float | VAr | W | change | PV |  | DINV | VArSpt | APC | ctlVal
CTRL_PARA | PV-Inverter | Requested reactive power setpoint of the inverter | float | VAr | R | change & integrity | PV |  | DINV | VArSpt | APC | mxVal | MX
SETTING | PV-Inverter | Inverter control source: current, voltage, voltagecurrent | enumeration | / | R/W | change | PV |  | DINV | InvCtlSrc | ENG | setVal | SP | InverterControlSourceKind
SETTING | PV-Inverter | Rated active power of the inverter | float | W | R/W | change | PV |  | DINV | WRtg | ASG | setMag | SP
SETTING | PV-Inverter | The continuous apparent power capability of the power inverter. | float | VAr | R/W | change | PV |  | DINV | VARtg | ASG | setMag | SP
CTRL_PARA | PV-Inverter | PQV set of limiting curves. | Curve | / | R/W | change | PV |  | DINV | WVArVLim | CSG
CTRL_PARA | PV-Inverter | Active curve characteristic curve for PQV limit. | Curve | / | R/W | change | PV |  | DINV | WVArVLimSet | CSG
SETTING | PV-Inverter | Nominal frequency of switching. | float | Hz | R/W | change | PV |  | DINV | SwHz | ASG | setMag | SP
SETTING | PV-Inverter | Type of isolation. |  |  |  |  | PV |  | DINV | IsoTyp | ENG | setVal | SP | isolationKind
SETTING | PV-Inverter | Type of AC system. | Float | W | R | initial | PV |  | DINV | ACTyp | ENG | setVal | SP | ACSystemKind
SETTING | PV-Inverter | Maximum Input current limit. | String | / | R | initial | PV |  | DINV | InAMax | ENG | setVal | SP
SETTING | PV-Inverter | Maximum Input voltage limit. | float | / | R | Change | PV |  | DINV | InVMax | ASG | setVal | SP
SETTING | PV-Inverter | Rated bidirectional reactive power. | float | / | R | Change | PV |  | DINV | VArRtg | ASG | setVal | SP
SETTING | PV-Inverter | Rated voltage (intrinsic property) | float | / | R/W | Change | PV |  | DINV | VRtg | ASG | setVal | SP
OTHER | PV-Inverter | Pdc0, DC power level at which the AC power rating is achieved at the reference operating condition - OPTIONAL | float | W | R | Initial
OTHER | PV-Inverter | Vdc0, DC voltage level at which the AC power rating is achieved at reference operating conditions - OPTIONAL | float | V | R | Initial
OTHER | PV-Inverter | Ps0, DC power required to start the inversion process, or self-consumption by inverter, strongly influences inverter efficiency at low power levels - OPTIONAL | float | W | R | Initial
OTHER | PV-Inverter | C0, Parameter defining the curvature of the relationship between AC output power and DC input power - OPTIONAL | float |  | R | Initial
OTHER | PV-Inverter | C1, Parameter defining the curvature of the relationship between AC output power and DC input power - OPTIONAL | float |  | R | Initial
OTHER | PV-Inverter | C2, Parameter defining the curvature of the relationship between AC output power and DC input power - OPTIONAL | float |  | R | Initial
OTHER | PV-Inverter | C3, Parameter defining the curvature of the relationship between AC output power and DC input power - OPTIONAL | float |  | R | Initial
OTHER | PV-Inverter | Pnt, Night power consumption. - OPTIONAL | float | W | R | Initial
OTHER | PV-Inverter | Number of MPPT inputs. - OPTIONAL | unsigned integer |  | R | Initial
FLEX_INFO | PV-Inverter | A list of flexibility market partner ID | character | / |  | Initial | PV |  | DCCT | NamPlt | LPL | vendor | DC
FLEX_INFO | PV-Inverter | A list of flexibility purchaser priority | character | / |  | Initial | PV |  | DCCT | NamPlt | LPL | swRev | DC
FLEX_INFO | PV-Inverter | Registered flexibility platform | character | / |  | Initial | PV |  | DCCT | NamPlt | LPL | d | DC
FLEX_INFO | PV-Inverter | Currently activated flexibility purchaser | character | / |  | Initial | PV |  | DCCT | NamPlt | LPL | configRev | DC
FLEX_INFO | PV-Inverter | ISO 4217 currency 3-character code | character | / |  | change | PV |  | DCCT | Ccy | CUG | cur | SP
FLEX_INFO | PV-Inverter | Marginal operational cost per hour | float | cur |  | change | PV |  | DCCT | OpCost | ASG | setMag | SP
FLEX_INFO | PV-Inverter | Marginal operational cost per kWh | float | cur |  | change | PV |  | DCCT | OpWhCost | ASG | setMag | SP
FLEX_INFO | PV-Inverter | Cost to start up DER | float | cur |  | change | PV |  | DCCT | StrCost | ASG | setMag | SP
FLEX_INFO | PV-Inverter | Cost to stop DER | float | cur |  | change | PV |  | DCCT | StopCost | ASG | setMag | SP
FLEX_INFO | PV-Inverter | Cost to ramp DER per kW per minute | float | cur |  | change | PV |  | DCCT | RampCost | ASG | setMag | SP
FLEX_INFO | PV-Inverter | Incremental heat rate piecewise linear curve costs. | Curve | / |  | change | PV |  | DCCT | HeatRteCost | CSG
FLEX_INFO | PV-Inverter | Incremental carbon emission curve costs. | Curve | / |  | change | PV |  | DCCT | CRteCost | CSG
MKT_IF | PV-Inverter | A list of energy market partner ID | character | / |  | Initial | PV |  | DCST | NamPlt | LPL | vendor | DC
MKT_IF | PV-Inverter | A list of energy purchaser priority | character | / |  | Initial | PV |  | DCST | NamPlt | LPL | swRev | DC
MKT_IF | PV-Inverter | Registered energy platform | character | / |  | Initial | PV |  | DCST | NamPlt | LPL | d | DC
MKT_IF | PV-Inverter | Currently activated energy purchaser | character | / |  | Initial | PV |  | DCST | NamPlt | LPL | configRev | DC
MKT_IF | PV-Inverter | ISO 4217 currency 3-character code | character | / |  | change | PV |  | DCST | Ccy | CUG | cur | SP
MKT_IF | PV-Inverter | Cost to start up DER | float | cur |  | change | PV |  | DCST | StrCost | ASG | setMag | SP
MKT_IF | PV-Inverter | Cost to stop DER | float | cur |  | change | PV |  | DCST | StopCost | ASG | setMag | SP
MKT_IF | PV-Inverter | Cost to ramp DER per kW per minute | float | cur |  | change | PV |  | DCST | RampCost | ASG | setMag | SP
MKT_IF | PV-Inverter | Incremental carbon emission curve costs. | Curve | / |  | change | PV |  | DCST | CRteCost | CSG
MKT_IF | PV-Inverter | Active curve characteristics for the incremental heat rate curve | Curve | / |  | change | PV |  | DCST | HeatRteAct | CSG
MKT_IF | PV-Inverter | Incremental heat rate piecewise linear curve costs. | Curve | / |  | change | PV |  | DCST | HeatRteCost | CSG
HW_META | PV-Inverter | measuring unit vendor | character | / | R | Initial | PV |  | MMXU | NamPlt | LPL | vendor | DC
HW_META | PV-Inverter | measuring unit software version | character | / | R | Initial | PV |  | MMXU | NamPlt | LPL | swRev | DC
HW_META | PV-Inverter | measuring unit description | character | / | R | Initial | PV |  | MMXU | NamPlt | LPL | d | DC
HW_META | PV-Inverter | A placeholder for later use | character | / | R | Initial | PV |  | MMXU | NamPlt | LPL | configRev | DC
STAT_INFO | PV-Inverter | status of the power vector expressed through one of the 9 zones of the PQ diagram quadrant, based on the signing conventions set with PFSign and PFExt. | enumeration | / | R | change | PV |  | MMXU | PQSt | ENS | stVal | ST | QuadrantRunningStateKind
MEAS_VAL | PV-Inverter | total active power measurement | float | W | R | change & integrity | PV |  | MMXU | TotW | MV | mag | MX
MEAS_VAL | PV-Inverter | total reactive power measurement | float | Var | R | change & integrity | PV |  | MMXU | TotVar | MV | mag | MX
MEAS_VAL | PV-Inverter | total apparent power measurement | float | VA | R | change & integrity | PV |  | MMXU | TotVA | MV | mag | MX
MEAS_VAL | PV-Inverter | ratio of the absolute active power to the apparent power | float | / | R | change & integrity | PV |  | MMXU | TotPF | MV | mag | MX
MEAS_VAL | PV-Inverter | frequency | float | Hz | R | change & integrity | PV |  | MMXU | Hz | MV | mag | MX
MEAS_VAL | PV-Inverter | Phase to phase voltages. | float | V | R | change & integrity | PV |  | MMXU | PPV | DEL | phsAB/BC/CA.cVal.mag | MX
MEAS_VAL | PV-Inverter | Phase to neutral voltages. | float | V | R | change & integrity | PV |  | MMXU | PNV | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PV-Inverter | Phase to ground (line) voltages. | float | V | R | change & integrity | PV |  | MMXU | PhV | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PV-Inverter | Phase to ground/phase to neutral three phase currents. | float | A | R | change & integrity | PV |  | MMXU | A | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PV-Inverter | Phase to ground/phase to neutral real powers P. | float | W | R | change & integrity | PV |  | MMXU | W | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PV-Inverter | Phase to ground/phase to neutral reactive powers Q. | float | Var | R | change & integrity | PV |  | MMXU | VAr | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PV-Inverter | Phase to ground/phase to neutral apparent powers S. | float | VA | R | change & integrity | PV |  | MMXU | VA | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PV-Inverter | Phase to ground/phase to neutral signed power factors. | float | / | R | change & integrity | PV |  | MMXU | PF | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PV-Inverter | Phase to ground/phase to neutral impedances in a three-phase system. | float | ohm | R | change & integrity | PV |  | MMXU | Z | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | PV-Inverter | Rate of change of frequency | float | Hz/s | R | change & integrity | PV |  | MMXU | HzRte | MV | mag | MX
MEAS_VAL | PV-Inverter | Arithmetic average of the magnitude of current of the 3 phases: average(Ia,Ib,Ic). | float | A | R | change & integrity | PV |  | MMXU | AvAPhs | MV | mag | MX
MEAS_VAL | PV-Inverter | Arithmetic average of the magnitude of phase to phase voltage of the 3 phases: average(PPVa, PPVb, PPVc). | float | V | R | change & integrity | PV |  | MMXU | AvPPVPhs | MV | mag | MX
MEAS_VAL | PV-Inverter | Arithmetic average of the magnitude of phase to reference voltage of the 3 phases: average(PhVa, PhVb, PhVc). | float | V | R | change & integrity | PV |  | MMXU | AvPhVPhs | MV | mag | MX
MEAS_VAL | PV-Inverter | Arithmetic average of the magnitude of active power of the 3 phases: average(Wa, Wb, Wc). | float | W | R | change & integrity | PV |  | MMXU | AvWPhs | MV | mag | MX
MEAS_VAL | PV-Inverter | Arithmetic average of the magnitude of apparent power of the 3 phases: average(VAa, VAb, VAc). | float | Var | R | change & integrity | PV |  | MMXU | AvVAPhs | MV | mag | MX
MEAS_VAL | PV-Inverter | Arithmetic average of the magnitude of reactive power of the 3 phases: average(VAra, VArb, VArc). | float | VA | R | change & integrity | PV |  | MMXU | AvVArPhs | MV | mag | MX
MEAS_VAL | PV-Inverter | Arithmetic average of the magnitude of power factor of the 3 phases: average(PFa, PFb, PFc). | float | / | R | change & integrity | PV |  | MMXU | AvPFPhs | MV | mag | MX
MEAS_VAL | PV-Inverter | Arithmetic average of the magnitude of impedance of the 3 phases: average(Za, Zb, Zc). | float | ohm | R | change & integrity | PV |  | MMXU | AvZPhs | MV | mag | MX
MEAS_VAL | PV-Inverter | meter vendor | character | / | R | Initial | PV |  | MMTR | NamPlt | LPL | vendor | DC
MEAS_VAL | PV-Inverter | meter software version | character | / | R | Initial | PV |  | MMTR | NamPlt | LPL | swRev | DC
MEAS_VAL | PV-Inverter | meter description | character | / | R | Initial | PV |  | MMTR | NamPlt | LPL | d | DC
MEAS_VAL | PV-Inverter | meter configuration revision | character | / | R | Initial | PV |  | MMTR | NamPlt | LPL | configRev | DC
MEAS_VAL | PV-Inverter | Net apparent energy since last reset. | integer | VAh | R | change & integrity | PV |  | MMTR | TotVAh | BCR | actVal | ST
MEAS_VAL | PV-Inverter | Net real energy since last reset. | integer | Wh | R | change & integrity | PV |  | MMTR | TotWh | BCR | actVal | ST
MEAS_VAL | PV-Inverter | Net reactive energy since last reset. | integer | VArh | R | change & integrity | PV |  | MMTR | TotVArh | BCR | actVal | ST
MEAS_VAL | PV-Inverter | Real energy supply (default direction: towards busbar). | integer | Wh | R | change & integrity | PV |  | MMTR | SupWh | BCR | actVal | ST
MEAS_VAL | PV-Inverter | Reactive energy supply (default direction: towards busbar). | integer | VArh | R | change & integrity | PV |  | MMTR | SupVArh | BCR | actVal | ST
MEAS_VAL | PV-Inverter | Real energy demand (direction: from busbar). | integer | Wh | R | change & integrity | PV |  | MMTR | DmdWh | BCR | actVal | ST
MEAS_VAL | PV-Inverter | Reactive energy demand (direction: from busbar). | integer | VArh | R | change & integrity | PV |  | MMTR | DmdVArh | BCR | actVal | ST
SCHD_INFO | PV-Inverter | PV active power forecast schedule provider | character | / | R | Initial | PV | PVCTL_ | FSCH | NamPlt | LPL | vendor | DC
SCHD_INFO | PV-Inverter | PV active power forecast schedule revision | character | / | R | Initial | PV | PVCTL_ | FSCH | NamPlt | LPL | swRev | DC
SCHD_INFO | PV-Inverter | PV active power forecast schedule description | character | / | R | Initial | PV | PVCTL_ | FSCH | NamPlt | LPL | d | DC
SCHD_INFO | PV-Inverter | A placeholder for later use | character | / | R | Initial | PV | PVCTL_ | FSCH | NamPlt | LPL | configRev | DC
SCHD_INFO | PV-Inverter | State of this schedule | enumeration | / | R | change | PV | PVCTL_ | FSCH | SchdSt | ENS | stVal | ST | ScheduleStateKind
SCHD_INFO | PV-Inverter | The current schedule entry of a running schedule. This is the Data-Instance-ID of the data object ValXXX (e.g. ValASG). As long as the schedule is not running the value shall be 0. | integer | / | R | change | PV | PVCTL_ | FSCH | SchdEntr | INS | stVal | ST
SCHD_INFO | PV-Inverter | The time when the schedule started running. If the schedule is not running, the quality of the value is set to invalid. | timestamp | / | R | change | PV | PVCTL_ | FSCH | ActStrTm | TCS | stVal | ST
SCHD_INFO | PV-Inverter | The next time when the schedule is planned/intented to start or re-start running. If no schedules are planned running, the quality of the value is set to invalid. | timestamp | / | R | change | PV | PVCTL_ | FSCH | NxtStrTm | TCS | stVal | ST
SCHD_INFO | PV-Inverter | Enumeration reflecting the potential error which has happened at the latest Schedule Enabling request | enumeration | / | R | change | PV | PVCTL_ | FSCH | SchdEnaErr | ENS | stVal | ST | ScheduleEnablingErrorKind
SCHD_INFO | PV-Inverter | Current value determined by the schedule. As long as the schedule is not running the quality of the value is invalid. The unit of this data shall be the same as the unit of the data object(s) ValASG | float | / | R | change | PV | PVCTL_ | FSCH | ValMV | MV | mag | MX
SCHD_INFO | PV-Inverter | (controllable) Operating with value true initiates enable transition request according to the state diagram; operating with value false is ignored. The change of its status value is a local issue. | boolean | / | R/W | change | PV | PVCTL_ | FSCH | EnaReq | SPC | ctlVal
SCHD_INFO | PV-Inverter | (controllable) Operating with value true initiates disable transition request according to the state diagram; operating with value false is ignored. The change of its status value is a local issue. | boolean | / | R/W | change | PV | PVCTL_ | FSCH | DsaReq | SPC | ctlVal
SCHD_INFO | PV-Inverter | The priority relation of this schedule (0..n) with higher numbers superseding lower numbers. Shall be a positive value. If missing the default is zero. | unsigned integer | / | R/W | change | PV | PVCTL_ | FSCH | SchdPrio | ING | setVal | SP
SCHD_INFO | PV-Inverter | The number of schedule entries that are valid out of the instantiated ValASG, ValING, ValSPG or ValENG. NumEntr shall be > 0. NumEntr is <= number of instantiated Val[ASG¦ING¦SPG¦ENG]'s | unsigned integer | / | R/W | change | PV | PVCTL_ | FSCH | NumEntr | ING | setVal | SP
SCHD_INFO | PV-Inverter | The schedule interval duration in time entities as specified in the unit. The SIUnit is mandatory in this data object. The total duration of a schedule shall be (NumEntr x SchdIntv). | unsigned integer | s | R/W | change | PV | PVCTL_ | FSCH | SchdIntv | ING | setVal | SP
SCHD_INFO | PV-Inverter | The ASG scheduled values (current value output as MV). Multiple entries should be possible. | float | / | R/W | change | PV | PVCTL_ | FSCH | ValASG | ASG | setMag | SP
SCHD_INFO | PV-Inverter | Start time of the schedule in UTC time. | timestamp | / | R/W | change | PV | PVCTL_ | FSCH | StrTm | TSG | setTm | SP
SCHD_INFO | PV-Inverter | If true, the change of the schedule to the running and activated state is triggered by an external event and not by the start time. The external event is referenced through 'InSyn'. | boolean | / | R/W | change | PV | PVCTL_ | FSCH | EvtTrg | SPG | setVal | SP
SCHD_INFO | PV-Inverter | Object reference of the external trigger if the schedule is triggered by an event. | objectReference | / | R/W | change | PV | PVCTL_ | FSCH | InSyn | ORG | setSrcRef | SP
SCHD_INFO | PV-Inverter | If true, once terminated or disabled, the schedule will change to the validated state, otherwise it will change to the not ready state. | boolean | / | R/W | change | PV | PVCTL_ | FSCH | SchdReuse | SPG | setVal | SP
SCHD_INFO | PV-Inverter | Object reference of data object bound to the input n. | objectReference | / | R/W | change | PV | PVCTL_ | FSCH | InRef | ORG | setSrcRef | SP
SCHD_INFO | PV-Inverter | PV active power forecast schedule controller manager | character | / | R | Initial | PV | PVCTL_ | FSCC | NamPlt | LPL | vendor | DC
SCHD_INFO | PV-Inverter | PV active power forecast schedule controller revision | character | / | R | Initial | PV | PVCTL_ | FSCC | NamPlt | LPL | swRev | DC
SCHD_INFO | PV-Inverter | PV active power forecast schedule controller description | character | / | R | Initial | PV | PVCTL_ | FSCC | NamPlt | LPL | d | DC
SCHD_INFO | PV-Inverter | A placeholder for later use | character | / | R | Initial | PV | PVCTL_ | FSCC | NamPlt | LPL | configRev | DC
SCHD_INFO | PV-Inverter | Indication of which schedule is active as an object reference. As long as no schedule is active the quality of the value is invalid. The active schedule is selected by the schedule controller within the running schedules based on the priority of the running schedules. | objectReference | / | R | change | PV | PVCTL_ | FSCC | ActSchdRef | ORS | stVal | ST
SCHD_INFO | PV-Inverter | Current value determined by the schedule. As long as the schedule is not running the quality of the value shall be set to invalid. The unit of this data shall be the same as the unit of the data object(s) FSCH.ValASG. | float | W | R | change | PV | PVCTL_ | FSCC | ValMV | MV | mag | MX
SCHD_INFO | PV-Inverter | Object reference to the entity controlled by the schedule. | objectReference | / | R/W | change | PV | PVCTL_ | FSCC | CtlEnt | ORG | setSrcRef | SP
SCHD_INFO | PV-Inverter | Object reference of schedule n (an LN reference to the LN of class FSCH). | objectReference | / | R/W | change | PV | PVCTL_ | FSCC | Schd | ORG | setSrcRef | SP
SCHD_INFO | PV-Inverter | Object reference of data object bound to the input n. | objectReference | / | R/W | change | PV | PVCTL_ | FSCC | InRef | ORG | setSrcRef | SP
SW_META | ECP | Name plate of the logical node | character | / | R | Initial | STO |  | LLN0 | NamPlt | LPL | vendor | DC
SW_META | ECP | Name plate of the logical node | character | / | R | Initial | STO |  | LLN0 | NamPlt | LPL | swRev | DC
SW_META | ECP | Name plate of the logical node | character | / | R | Initial | STO |  | LLN0 | NamPlt | LPL | d | DC
SW_META | ECP | A placeholder for later use | character | / | R | Initial | STO |  | LLN0 | NamPlt | LPL | configRev | DC
STAT_INFO | ECP | ECP data service failure description | character | / | R | Change | STO |  | LLN0 | Beh | ENS | d | DC
SW_META | ECP | ECP service provider | character | / | R | Initial | STO |  | DECP | NamPlt | LPL | vendor | DC
SW_META | ECP | ECP service software version | character | / | R | Initial | STO |  | DECP | NamPlt | LPL | swRev | DC
SW_META | ECP | ECP service description | character | / | R | Initial | STO |  | DECP | NamPlt | LPL | d | DC
SW_META | ECP | A placeholder for later use | character | / | R | Initial | STO |  | DECP | NamPlt | LPL | configRev | DC
STAT_INFO | ECP | Type of circuit phases | enumeration | / | R | Initial | STO |  | DECP | PhsConnTyp | ENS | stVal | ST | PhaseKind
SETTING | ECP | Default reference voltage for functions using voltage at this ECP as input | float | V | R/W | change | STO |  | DECP | VRef | ASG | setMag | SP
SETTING | ECP | Percent of VRef to use in calculating the voltage to use in operational function calculations | float | % | R/W | change | STO |  | DECP | VRefPct | ASG | setMag | SP
SETTING | ECP | Electrical active power rating at ECP | float | W | R/W | change | STO |  | DECP | WRtg | ASG | setMag | SP
SETTING | ECP | Reactive power rating at ECP | float | Var | R/W | change | STO |  | DECP | VArRtg | ASG | setMag | SP
SETTING | ECP | Apparent power rating at ECP | float | VA | R/W | change | STO |  | DECP | VARtg | ASG | setMag | SP
SETTING | ECP | Voltage rating at ECP | float | V | R/W | change | STO |  | DECP | VRtg | ASG | setMag | SP
SETTING | ECP | Nominal frequency at ECP | float | Hz | R/W | change | STO |  | DECP | HzNom | ASG | setMag | SP
SETTING | ECP | Rated maximum voltage | float | V | R/W | change | STO |  | DECP | VMax | ASG | setMag | SP
SETTING | ECP | Rated minimum voltage | float | V | R/W | change | STO |  | DECP | Vmin | ASG | setMag | SP
CTRL_PARA | ECP | Identity of electrical reference point as a Visible String | character | / | R/W | change | STO |  | DECP | ElcRefId | VSG | setVal | SP
CTRL_PARA | ECP | Indication whether the active power from the DER referencing this ECP is included in the measurements coming from the ECP. This is important for managing Generation and Load Following, as well as Peak Power Limiting functions. | boolean | / | R | change | STO |  | DECP | DERMsIncl | SPG | setVal | SP
HW_META | Electrical storage | Storage system name | character | / | R | Initial | STO |  | DSTO | EEName | DPL | name | DC
HW_META | Electrical storage | Storage system hardware vendor | character | / | R | Initial | STO |  | DSTO | EEName | DPL | vendor | DC
HW_META | Electrical storage | Storage system hardware model | character | / | R | Initial | STO |  | DSTO | EEName | DPL | model | DC
HW_META | Electrical storage | Storage system hardware serial number | character | / | R | Initial | STO |  | DSTO | EEName | DPL | serNum | DC
SW_META | Electrical storage | Storage system software revision | character | / | R | Initial | STO |  | DSTO | EEName | DPL | swRev | DC
HW_META | Electrical storage | Storage system owner | character | / | R | Initial | STO |  | DSTO | EEName | DPL | owner | DC
HW_META | Electrical storage | Storage system connected electrical power system | character | / | R | Initial | STO |  | DSTO | EEName | DPL | ePSName | DC
HW_META | Electrical storage | Storage system primary operator | character | / | R | Initial | STO |  | DSTO | EEName | DPL | primeOper | DC
HW_META | Electrical storage | Storage system secondary operator | character | / | R | Initial | STO |  | DSTO | EEName | DPL | secondOper | DC
STAT_INFO | Electrical storage | Storage system hardware reversion | character | / | R | Change | STO |  | DSTO | EEName | DPL | hwRev | DC
STAT_INFO | Electrical storage | Storage system hardware UUID | character | / | R | Initial | STO |  | DSTO | EEName | DPL | mRID | DC
STAT_INFO | Electrical storage | Storage system hardware description | character | / | R | Change | STO |  | DSTO | EEName | DPL | d | DC
STAT_INFO | Electrical storage | Name plate of the logical node | character | / | R | Initial | STO |  | DSTO | NamPlt | LPL | vendor | DC
STAT_INFO | Electrical storage | Name plate of the logical node | character | / | R | Initial | STO |  | DSTO | NamPlt | LPL | swRev | DC
STAT_INFO | Electrical storage | Name plate of the logical node | character | / | R | Initial | STO |  | DSTO | NamPlt | LPL | d | DC
STAT_INFO | Electrical storage | A placeholder for later use | character | / | R | Initial | STO |  | DSTO | NamPlt | LPL | configRev | DC
STAT_INFO | Electrical storage | Alarm trigger status: if true, the maximum state of charge threshold of the battery (SocHiAlsPct) has been exceeded | boolean | / | R | change | STO |  | DSTO | SocHiAlm | SPS | stVal | ST
STAT_INFO | Electrical storage | Warning trigger status: if true, the high state of charge warning threshold of the battery has been exceeded | boolean | / | R | change | STO |  | DSTO | SocHiWrn | SPS | stVal | ST
STAT_INFO | Electrical storage | Alarm trigger status: If true,the minimum state of charge threshold of the battery (SocLoAlsPct) has been exceeded | boolean | / | R | change | STO |  | DSTO | SocLoAlm | SPS | stVal | ST
STAT_INFO | Electrical storage | Warning trigger status: if true, the low state of charge warning threshold of the battery has been exceeded | boolean | / | R | change | STO |  | DSTO | SocLoWrn | SPS | stVal | ST
STAT_INFO | Electrical storage | Alarm trigger status: If true, the predefined threshold of the low state of health of the storage resource (SohLoAlsPct) has been reached | boolean | / | R | change | STO |  | DSTO | SohLoAlm | SPS | stVal | ST
STAT_INFO | Electrical storage | Count of the number of equivalent full charge cycles | integer | / | R | change | STO |  | DSTO | ChaCycCnt | INS | stVal | ST
STAT_INFO | Electrical storage | Current state of operation of the distributed energy resource. | enumeration | / | R | change | STO |  | DSTO | DEROpSt | ENS | stVal | ST | DERStateKind
STAT_INFO | Electrical storage | State of external (electrical, mechanical or communication) equipment to which the logical node is associated. | enumeration | / | R | change | STO |  | DSTO | EEHealth | ENS | stVal | ST | HealthKind
STAT_INFO | Electrical storage | Operation time of the external (electrical,mechanical or communication) equipment sincestart of the operation. | integer | h | R | change | STO |  | DSTO | OpTmh | INS | stVal | ST
FLEX_INFO | Electrical storage | Available energy capacity to be charged (in Wh) | float | Wh | R | change | STO |  | DSTO | InWh | MV | mag | MX
FLEX_INFO | Electrical storage | Energy stored and available for discharging (in Wh) | float | Wh | R | change | STO |  | DSTO | OutWh | MV | mag | MX
MEAS_VAL | Electrical storage | state of charge expressed in Wh | float | Wh | R | change | STO |  | DSTO | SocWh | MV | mag | MX
FLEX_INFO | Electrical storage | Usable state of charge (expressed as percent of total usable energy capacity UseWh) which may be directly measured or calculated | float | % | R | change | STO |  | DSTO | UseSocPct | MV | mag | MX
FLEX_INFO | Electrical storage | State of charge as percentage in relation to the effective energy capacity of the storage resource with respect to the degradation so far (EffWh). | float | % | R | change | STO |  | DSTO | SocEffWhPct | MV | mag | MX
MEAS_VAL | Electrical storage | Total Energy Charged since last reset (in Wh) | float | Wh | R | change | STO |  | DSTO | ChaWhTot | MV | mag | MX
MEAS_VAL | Electrical storage | Total Energy Discharged since last reset | float | Wh | R | change | STO |  | DSTO | DschWhTot | MV | mag | MX
FLEX_INFO | Electrical storage | Available power | float | W | R | change | STO |  | DSTO | AvlDschW | MV | mag | MX
FLEX_INFO | Electrical storage | Available charging power | float | W | R | change | STO |  | DSTO | AvlChaW | MV | mag | MX
MEAS_VAL | Electrical storage | Actual volt-amps percentage charged based on ChaVAMax | float | % | R | change | STO |  | DSTO | ChaVAPct | MV | mag | MX
FLEX_INFO | Electrical storage | available charging time | float | s | R | change | STO |  | DSTO | AvlChaWTm | MV | mag | MX
FLEX_INFO | Electrical storage | Available discharging time | float | s | R | change | STO |  | DSTO | AvlDschWTm | MV | mag | MX
FLEX_INFO | Electrical storage | The total amount of reactive power available for absorbing even if possibly impacting active power output while charging | float | VAr | R | change | STO |  | DSTO | ChaAvarTot | MV | mag | MX
FLEX_INFO | Electrical storage | The total amount of reactive power available for absorbing even if possibly impacting active power output while discharging. | float | VAr | R | change | STO |  | DSTO | DschAvarTot | MV | mag | MX
FLEX_INFO | Electrical storage | The total amount of reactive power available for injecting even if possibly impacting active power output while charging | float | VAr | R | change | STO |  | DSTO | ChaIvarTot | MV | mag | MX
FLEX_INFO | Electrical storage | The total amount of reactive power available for injecting even if possibly impacting active power output while discharging | float | VAr | R | change | STO |  | DSTO | DschIvarTot | MV | mag | MX
FLEX_INFO | Electrical storage | The amount of reactive power available for absorbing without impacting active power output while charging | float | VAr | R | change | STO |  | DSTO | ChaAvarAvl | MV | mag | MX
FLEX_INFO | Electrical storage | The amount of reactive power available for absorbing without impacting active power output while discharging | float | VAr | R | change | STO |  | DSTO | DschAvarAvl | MV | mag | MX
FLEX_INFO | Electrical storage | The amount of reactive power available for injecting without impacting active power output while charging | float | VAr | R | change | STO |  | DSTO | ChaIvarAvl | MV | mag | MX
FLEX_INFO | Electrical storage | The amount of reactive power available for injecting without impacting active power output while discharging | float | VAr | R | change | STO |  | DSTO | DschIvarAvl | MV | mag | MX
STAT_INFO | Electrical storage | Effective actual total energy capacity (in Wh) provided by the storage resource. Due to degradation, the amount may be less than the rated total energy capacity (WhRtg). | float | Wh | R | change | STO |  | DSTO | EffWh | MV | mag | MX
STAT_INFO | Electrical storage | Effective actual total energy capacity (expressed as percentage of WhRtg) provided by the storage resource. Due to degradation, the amount may be less than the rated total energy capacity (WhRtg). In case both WhEffCapPct and WhEffCap DOs are present in a same LN instance, the application shall ensure to keep the values of both DOs consistent. | float | % | R | change | STO |  | DSTO | EffWhPct | MV | mag | MX
MEAS_VAL | Electrical storage | Actual self service energy used | float | Wh | R | change | STO |  | DSTO | SelfSvcWh | MV | mag | MX
MEAS_VAL | Electrical storage | Actual percentage of apparent power output based on VAMax | float | % | R | change | STO |  | DSTO | VAPct | MV | mag | MX
FLEX_INFO | Electrical storage | Available capability (measured or calculated) for increasing active output, including increasing generation of active power, even if currently consuming power. | float | W | R | change | STO |  | DSTO | AvlUpW | MV | mag | MX
MEAS_VAL | Electrical storage | Available capability (measured or calculated) for decreasing active power, including increasing the consumption of active power, even if currently generating power. | float | W | R | change | STO |  | DSTO | AvlDnW | MV | mag | MX
CTRL_PARA | Electrical storage | Operating with the value expressed in ctlVal (selected among the list specified in DERStateControlKind) initiates the appropriate transition request. The reading of its attribute stVal is meaningless. The resulting state of the DER shall be observed in the DEROpSt DO. | enumeration | / | W | change | STO |  | DSTO | DEROpStCtl | ENC |  |  | DERStateTransitionKind
CTRL_PARA | Electrical storage | Active power setpoint. | float | W | W | change | STO |  | DSTO | WSpt | APC | ctlVal
CTRL_PARA | Electrical storage | Active power setpoint that is requested. | float | W | R | change & integrity | STO |  | DSTO | WSpt | APC | mxVal | MX
CTRL_PARA | Electrical storage | Reactive power setpoint. | float | VAr | W | change | STO |  | DSTO | VArSpt | APC | ctlVal
CTRL_PARA | Electrical storage | Reactive power setpoint that is requested. | float | VAr | R | change & integrity | STO |  | DSTO | VArSpt | APC | mxVal | MX
STAT_INFO | Electrical storage | Operations count, can be reset to a value different than 0. | integer | / | R | change | STO |  | DSTO | OpCntRs | INC | stVal | ST
SETTING | Electrical storage | High state of charge alarm threshold of the battery (in percent) | float | % | R/W | change | STO |  | DSTO | SocHiAlsPct | ASG | setMag | SP
SETTING | Electrical storage | Warning high state of charge threshold of the battery (in percent) | float | % | R/W | change | STO |  | DSTO | SocHiWrsPct | ASG | setMag | SP
SETTING | Electrical storage | Low state of charge alarm threshold of the battery (in percent) | float | % | R/W | change | STO |  | DSTO | SocLoAlsPct | ASG | setMag | SP
SETTING | Electrical storage | Warning state of charge threshold of the battery (in percent) | float | % | R/W | change | STO |  | DSTO | SocLoWrsPct | ASG | setMag | SP
SETTING | Electrical storage | Threshold alarm setting of the usable lower limit of the storage resource (in % of the usable capacity of the storage element (in Wh) – CapWhUseRtg ) | float | % | R/W | change | STO |  | DSTO | SohLoAlsPct | ASG | setMag | SP
CTRL_PARA | Electrical storage | Roundtrip efficiency [%] at nominal conditions | float | % | R/W | change | STO |  | DSTO | RntEffPct | ASG | setMag | SP
CTRL_PARA | Electrical storage | Nameplate maximum active power rating while charging | float | W | R/W | change | STO |  | DSTO | ChaWMaxRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate maximum active power rating while discharging | float | W | R/W | change | STO |  | DSTO | DschWMaxRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate ramp rate for changes in active power while charging: percentage of WMax per second | float | W | R/W | change | STO |  | DSTO | ChaWRmpRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate ramp rate for changes in active power while discharging: percentage of WMax per second | float | W | R/W | change | STO |  | DSTO | DschWRmpRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate maximum apparent charging power rating | float | VA | R/W | change | STO |  | DSTO | ChaVAMaxRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate maximum apparent discharging power rating | float | VA | R/W | change | STO |  | DSTO | DschVAMaxRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate rating for maximum absorbing reactive power while charging | float | AVar | R/W | change | STO |  | DSTO | ChaAvarRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate rating for maximum absorbing reactive power while discharging | float | AVar | R/W | change | STO |  | DSTO | DschAvarRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate rating for maximum supply (injection) reactive power while charging | float | AVar | R/W | change | STO |  | DSTO | ChaIvarRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate rating for maximum supply (injection) reactive power while discharging | float | AVar | R/W | change | STO |  | DSTO | DschIvarRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate rating for maximum voltage while charging | float | V | R/W | change | STO |  | DSTO | ChaVMaxRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate rating for maximum voltage while discharging | float | V | R/W | change | STO |  | DSTO | DschVMaxRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate rating for minimum voltage while charging | float | V | R/W | change | STO |  | DSTO | ChaVMinRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate rating for minimum voltage while discharging | float | V | R/W | change | STO |  | DSTO | DschVMinRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate rating for maximum current under nominal voltage under nominal power factor while charging | float | A | R/W | change | STO |  | DSTO | ChaAMaxRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate rating for maximum current under nominal voltage under nominal power factor while discharging | float | A | R/W | change | STO |  | DSTO | DschAMaxRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate energy storage capacity rating in Wh | float | Wh | R/W | change | STO |  | DSTO | WhRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate maximum amount of energy (in Wh) to be stored in the storage resource for e.g. supporting long life and avoid faster degradation | float | Wh | R/W | change | STO |  | DSTO | WhMaxRtg | ASG | setMag | SP
SETTING | Electrical storage | Nameplate minimum amount of energy (in Wh) to be retained in the storage resource for e.g. supporting long life and avoid faster degradation or to ensure a reserve of energy stored for emergencies and other purposes. | float | Wh | R/W | change | STO |  | DSTO | WhMinRtg | ASG | setMag | SP
SETTING | Electrical storage | Charging efficiency curve rating [% over SoC] | Curve | / | R/W | change | STO |  | DSTO | ChaEfcRtg | CSG
SETTING | Electrical storage | Discharging efficiency curve rating [% over SoC] | Curve | / | R/W | change | STO |  | DSTO | DschEfcRtg | CSG
SETTING | Electrical storage | Net Energy Metering (NEM) Policy Mode which establishes whether the DER qualifies as renewable. Mode A = Storage may charge from the grid but may not discharge to the grid (acts only as load). Mode B = Storage may not charge from the grid but may discharge to the grid (charges from local energy source). Mode C = Storage may charge or discharge from the grid at will / in response to commands for location where there are no NEM integrity concerns. | enumeration | / | R/W | change | STO |  | DSTO | ChaSrcRtg | ENG | setVal | SP | ChargeSourceKind
SETTING | Electrical storage | Maximum active power while charging | float | W | R/W | change | STO |  | DSTO | ChaWMax | ASG | setMag | SP
SETTING | Electrical storage | Default ramp rate for changes in active power: percentage of WMax per second while charging | float | W | R/W | change | STO |  | DSTO | ChaWRmp | ASG | setMag | SP
SETTING | Electrical storage | Default ramp rate for changes in active power: percentage of WMax per second while discharging | float | W | R/W | change | STO |  | DSTO | DschWRmp | ASG | setMag | SP
SETTING | Electrical storage | Charging reactive power maximum | float | VAr | R/W | change | STO |  | DSTO | ChaVArMax | ASG | setMag | SP
SETTING | Electrical storage | Discharging reactive power maximum | float | VAr | R/W | change | STO |  | DSTO | DschVArMax | ASG | setMag | SP
SETTING | Electrical storage | Maximum apparent charging power | float | VA | R/W | change | STO |  | DSTO | ChaVAMax | ASG | setMag | SP
SETTING | Electrical storage | Operational setpoint for maximum apparent power while discharging | float | VA | R/W | change | STO |  | DSTO | DschVAMax | ASG | setMag | SP
SETTING | Electrical storage | Operational setpoint for maximum absorbing reactive power while charging | float | VAr | R/W | change | STO |  | DSTO | ChaAvarMax | ASG | setMag | SP
SETTING | Electrical storage | Operational setpoint for maximum absorbing reactive power while discharging | float | VAr | R/W | change | STO |  | DSTO | DschAvarMax | ASG | setMag | SP
SETTING | Electrical storage | Operational setpoint for maximum supply (injection) reactive power while charging | float | VAr | R/W | change | STO |  | DSTO | ChaIvarMax | ASG | setMag | SP
SETTING | Electrical storage | Operational setpoint for maximum supply (injection) reactive power while discharging | float | VAr | R/W | change | STO |  | DSTO | DschIvarMax | ASG | setMag | SP
SETTING | Electrical storage | Operational setting for maximum voltage while charging | float | V | R/W | change | STO |  | DSTO | ChaVMax | ASG | setMag | SP
SETTING | Electrical storage | Operational setpoint for maximum voltage while discharging | float | V | R/W | change | STO |  | DSTO | DschVMax | ASG | setMag | SP
SETTING | Electrical storage | Operational setting for minimum voltage while charging | float | V | R/W | change | STO |  | DSTO | ChaVMin | ASG | setMag | SP
SETTING | Electrical storage | Operational setpoint for minimum voltage while discharging | float | V | R/W | change | STO |  | DSTO | DschVMin | ASG | setMag | SP
SETTING | Electrical storage | Operational setting for maximum current under nominal voltage under nominal power factor while charging | float | A | R/W | change | STO |  | DSTO | ChaAMax | ASG | setMag | SP
SETTING | Electrical storage | Operational setpoint for maximum current under nominal voltage under nominal power factor while discharging | float | A | R/W | change | STO |  | DSTO | DschAMax | ASG | setMag | SP
SETTING | Electrical storage | Charging efficiency curve [% over SoC] | Curve | / | R/W | change | STO |  | DSTO | ChaEfc | CSG
SETTING | Electrical storage | Discharging efficiency curve [% over SoC] | Curve | / | R/W | change | STO |  | DSTO | DschEfc | CSG
SETTING | Electrical storage | The energy reserve level above which the storage system may be only be charged in emergency situations, expressed as a percentage of the usable capacity, WhUseCap. | float | % | R/W | change | STO |  | DSTO | UseWhMaxPct | ASG | setMag | SP
SETTING | Electrical storage | The energy reserve level below which the storage system may be only be discharged in emergency situations, expressed as a percentage of the usable capacity, WhUseCap. | float | % | R/W | change | STO |  | DSTO | UseWhMinPct | ASG | setMag | SP
SETTING | Electrical storage | Operational setpoint for usable energy storage capacity in Wh | float | Wh | R/W | change | STO |  | DSTO | UseWh | ASG | setMag | SP
SETTING | Electrical storage | Net Energy Metering (NEM) Policy Mode which establishes whether the DER qualifies as renewable. Mode A = Storage may charge from the grid but may not discharge to the grid (acts only as load). Mode B = Storage may not charge from the grid but may discharge to the grid (charges from local energy source). Mode C = Storage may charge or discharge from the grid at will / in response to commands for location where there are no NEM integrity concerns. | character | / | R/W | change | STO |  | DSTO | ChaSrc | ENG | setVal | SP | ChargeSourceKind
SETTING | Electrical storage | Source of charging storage: True = charge from renewable sources only, False = charge from any sources | boolean | / | R/W | change | STO |  | DSTO | RenChaEna | SPG | setVal | SP
SETTING | Electrical storage | Connection type of ECP: connection to DER (Point of Connection (PoC)), to load, within Local Electric Power System (Local EPS), Point of Common Coupling (PCC), or directly to Area EPS | enumeration | / | R/W | change | STO |  | DSTO | EcpConnTyp | ENG | setVal | SP | ECPConnKind
SETTING | Electrical storage | Phase type of electrical connection of the DER | enumeration | / | R/W | change | STO |  | DSTO | PhsConnTyp | ENG | setVal | SP | PhaseKind
SETTING | Electrical storage | Type of DER | enumeration | / | R/W | change | STO |  | DSTO | DERTyp | ENG | setVal | SP | DERUnitKind
SETTING | Electrical storage | Maximum temperature rating | float | °C | R/W | change | STO |  | DSTO | TmpMaxRtg | ASG | setMag | SP
SETTING | Electrical storage | Exposure to fault rates as percent of ?? | float | % | R/W | change | STO |  | DSTO | FltRtgPct | ASG | setMag | SP
SETTING | Electrical storage | Max fault current rating | float | A | R/W | change | STO |  | DSTO | FltAMaxRtg | ASG | setMag | SP
SETTING | Electrical storage | Selfservice voltage | float | V | R/W | change | STO |  | DSTO | SelfVRtg | ASG | setMag | SP
SETTING | Electrical storage | Max fault duration rating | integer | ms | R/W | change | STO |  | DSTO | FltDurMaxTms | ING | setVal | SP
SETTING | Electrical storage | Efficiency at rated capacity as percent | float | % | R/W | change | STO |  | DSTO | EfcRtgPct | ASG | setMag | SP
SETTING | Electrical storage | Rated Nominal frequency of usage of the DER | float | Hz | R/W | change | STO |  | DSTO | HzNomRtg | ASG | setMag | SP
SETTING | Electrical storage | Rated minimal frequency of usage of the DER | float | Hz | R/W | change | STO |  | DSTO | HzMinRtg | ASG | setMag | SP
SETTING | Electrical storage | Rated maximal frequency of usage of the DER | float | Hz | R/W | change | STO |  | DSTO | HzMaxRtg | ASG | setMag | SP
SETTING | Electrical storage | Internal identifier of the resource within a system which is using that resource. It complements the mRID defined as part of the EEname DO. Different DERIds may be defined for different system users. | character | / | R/W | change | STO |  | DSTO | DERId | VSG | setVal | SP
FLEX_INFO | Electrical storage | A list of flexibility market partner ID | character | / |  | Initial | STO |  | DCCT | NamPlt | LPL | vendor | DC
FLEX_INFO | Electrical storage | A list of flexibility purchaser priority | character | / |  | Initial | STO |  | DCCT | NamPlt | LPL | swRev | DC
FLEX_INFO | Electrical storage | Registered flexibility platform | character | / |  | Initial | STO |  | DCCT | NamPlt | LPL | d | DC
FLEX_INFO | Electrical storage | Currently activated flexibility purchaser | character | / |  | Initial | STO |  | DCCT | NamPlt | LPL | configRev | DC
FLEX_INFO | Electrical storage | ISO 4217 currency 3-character code | character | / |  | change | STO |  | DCCT | Ccy | CUG | cur | SP
FLEX_INFO | Electrical storage | Marginal operational cost per hour | float | cur |  | change | STO |  | DCCT | OpCost | ASG | setMag | SP
FLEX_INFO | Electrical storage | Marginal operational cost per kWh | float | cur |  | change | STO |  | DCCT | OpWhCost | ASG | setMag | SP
FLEX_INFO | Electrical storage | Cost to start up DER | float | cur |  | change | STO |  | DCCT | StrCost | ASG | setMag | SP
FLEX_INFO | Electrical storage | Cost to stop DER | float | cur |  | change | STO |  | DCCT | StopCost | ASG | setMag | SP
FLEX_INFO | Electrical storage | Cost to ramp DER per kW per minute | float | cur |  | change | STO |  | DCCT | RampCost | ASG | setMag | SP
FLEX_INFO | Electrical storage | Incremental heat rate piecewise linear curve costs. | Curve | / |  | change | STO |  | DCCT | HeatRteCost | CSG
FLEX_INFO | Electrical storage | Incremental carbon emission curve costs. | Curve | / |  | change | STO |  | DCCT | CRteCost | CSG
MKT_IF | Electrical storage | A list of energy market partner ID | character | / |  | Initial | STO |  | DCST | NamPlt | LPL | vendor | DC
MKT_IF | Electrical storage | A list of energy purchaser priority | character | / |  | Initial | STO |  | DCST | NamPlt | LPL | swRev | DC
MKT_IF | Electrical storage | Registered energy platform | character | / |  | Initial | STO |  | DCST | NamPlt | LPL | d | DC
MKT_IF | Electrical storage | Currently activated energy purchaser | character | / |  | Initial | STO |  | DCST | NamPlt | LPL | configRev | DC
MKT_IF | Electrical storage | ISO 4217 currency 3-character code | character | / |  | change | STO |  | DCST | Ccy | CUG | cur | SP
MKT_IF | Electrical storage | Cost to start up DER | float | cur |  | change | STO |  | DCST | StrCost | ASG | setMag | SP
MKT_IF | Electrical storage | Cost to stop DER | float | cur |  | change | STO |  | DCST | StopCost | ASG | setMag | SP
MKT_IF | Electrical storage | Cost to ramp DER per kW per minute | float | cur |  | change | STO |  | DCST | RampCost | ASG | setMag | SP
MKT_IF | Electrical storage | Incremental carbon emission curve costs. | Curve | / |  | change | STO |  | DCST | CRteCost | CSG
MKT_IF | Electrical storage | Active curve characteristics for the incremental heat rate curve | Curve | / |  | change | STO |  | DCST | HeatRteAct | CSG
MKT_IF | Electrical storage | Incremental heat rate piecewise linear curve costs. | Curve | / |  | change | STO |  | DCST | HeatRteCost | CSG
HW_META | Electrical storage | measuring unit vendor | character | / | R | Initial | STO |  | MMXU | NamPlt | LPL | vendor | DC
HW_META | Electrical storage | measuring unit software version | character | / | R | Initial | STO |  | MMXU | NamPlt | LPL | swRev | DC
HW_META | Electrical storage | measuring unit description | character | / | R | Initial | STO |  | MMXU | NamPlt | LPL | d | DC
HW_META | Electrical storage | A placeholder for later use | character | / | R | Initial | STO |  | MMXU | NamPlt | LPL | configRev | DC
STAT_INFO | Electrical storage | status of the power vector expressed through one of the 9 zones of the PQ diagram quadrant, based on the signing conventions set with PFSign and PFExt. | enumeration | / | R | change | STO |  | MMXU | PQSt | ENS | stVal | ST | QuadrantRunningStateKind
MEAS_VAL | Electrical storage | total active power measurement | float | W | R | change & integrity | STO |  | MMXU | TotW | MV | mag | MX
MEAS_VAL | Electrical storage | total reactive power measurement | float | Var | R | change & integrity | STO |  | MMXU | TotVar | MV | mag | MX
MEAS_VAL | Electrical storage | total apparent power measurement | float | VA | R | change & integrity | STO |  | MMXU | TotVA | MV | mag | MX
MEAS_VAL | Electrical storage | ratio of the absolute active power to the apparent power | float | / | R | change & integrity | STO |  | MMXU | TotPF | MV | mag | MX
MEAS_VAL | Electrical storage | frequency | float | Hz | R | change & integrity | STO |  | MMXU | Hz | MV | mag | MX
MEAS_VAL | Electrical storage | Phase to phase voltages. | float | V | R | change & integrity | STO |  | MMXU | PPV | DEL | phsAB/BC/CA.cVal.mag | MX
MEAS_VAL | Electrical storage | Phase to neutral voltages. | float | V | R | change & integrity | STO |  | MMXU | PNV | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Electrical storage | Phase to ground (line) voltages. | float | V | R | change & integrity | STO |  | MMXU | PhV | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Electrical storage | Phase to ground/phase to neutral three phase currents. | float | A | R | change & integrity | STO |  | MMXU | A | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Electrical storage | Phase to ground/phase to neutral real powers P. | float | W | R | change & integrity | STO |  | MMXU | W | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Electrical storage | Phase to ground/phase to neutral reactive powers Q. | float | Var | R | change & integrity | STO |  | MMXU | VAr | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Electrical storage | Phase to ground/phase to neutral apparent powers S. | float | VA | R | change & integrity | STO |  | MMXU | VA | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Electrical storage | Phase to ground/phase to neutral signed power factors. | float | / | R | change & integrity | STO |  | MMXU | PF | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Electrical storage | Phase to ground/phase to neutral impedances in a three-phase system. | float | ohm | R | change & integrity | STO |  | MMXU | Z | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Electrical storage | Rate of change of frequency | float | Hz/s | R | change & integrity | STO |  | MMXU | HzRte | MV | mag | MX
MEAS_VAL | Electrical storage | Arithmetic average of the magnitude of current of the 3 phases: average(Ia,Ib,Ic). | float | A | R | change & integrity | STO |  | MMXU | AvAPhs | MV | mag | MX
MEAS_VAL | Electrical storage | Arithmetic average of the magnitude of phase to phase voltage of the 3 phases: average(PPVa, PPVb, PPVc). | float | V | R | change & integrity | STO |  | MMXU | AvPPVPhs | MV | mag | MX
MEAS_VAL | Electrical storage | Arithmetic average of the magnitude of phase to reference voltage of the 3 phases: average(PhVa, PhVb, PhVc). | float | V | R | change & integrity | STO |  | MMXU | AvPhVPhs | MV | mag | MX
MEAS_VAL | Electrical storage | Arithmetic average of the magnitude of active power of the 3 phases: average(Wa, Wb, Wc). | float | W | R | change & integrity | STO |  | MMXU | AvWPhs | MV | mag | MX
MEAS_VAL | Electrical storage | Arithmetic average of the magnitude of apparent power of the 3 phases: average(VAa, VAb, VAc). | float | Var | R | change & integrity | STO |  | MMXU | AvVAPhs | MV | mag | MX
MEAS_VAL | Electrical storage | Arithmetic average of the magnitude of reactive power of the 3 phases: average(VAra, VArb, VArc). | float | VA | R | change & integrity | STO |  | MMXU | AvVArPhs | MV | mag | MX
MEAS_VAL | Electrical storage | Arithmetic average of the magnitude of power factor of the 3 phases: average(PFa, PFb, PFc). | float | / | R | change & integrity | STO |  | MMXU | AvPFPhs | MV | mag | MX
MEAS_VAL | Electrical storage | Arithmetic average of the magnitude of impedance of the 3 phases: average(Za, Zb, Zc). | float | ohm | R | change & integrity | STO |  | MMXU | AvZPhs | MV | mag | MX
MEAS_VAL | Electrical storage | meter vendor | character | / | R | Initial | STO |  | MMTR | NamPlt | LPL | vendor | DC
MEAS_VAL | Electrical storage | meter software version | character | / | R | Initial | STO |  | MMTR | NamPlt | LPL | swRev | DC
MEAS_VAL | Electrical storage | meter description | character | / | R | Initial | STO |  | MMTR | NamPlt | LPL | d | DC
MEAS_VAL | Electrical storage | meter configuration revision | character | / | R | Initial | STO |  | MMTR | NamPlt | LPL | configRev | DC
MEAS_VAL | Electrical storage | Net apparent energy since last reset. | integer | VAh | R | change & integrity | STO |  | MMTR | TotVAh | BCR | actVal | ST
MEAS_VAL | Electrical storage | Net real energy since last reset. | integer | Wh | R | change & integrity | STO |  | MMTR | TotWh | BCR | actVal | ST
MEAS_VAL | Electrical storage | Net reactive energy since last reset. | integer | VArh | R | change & integrity | STO |  | MMTR | TotVArh | BCR | actVal | ST
MEAS_VAL | Electrical storage | Real energy supply (default direction: towards busbar). | integer | Wh | R | change & integrity | STO |  | MMTR | SupWh | BCR | actVal | ST
MEAS_VAL | Electrical storage | Reactive energy supply (default direction: towards busbar). | integer | VArh | R | change & integrity | STO |  | MMTR | SupVArh | BCR | actVal | ST
MEAS_VAL | Electrical storage | Real energy demand (direction: from busbar). | integer | Wh | R | change & integrity | STO |  | MMTR | DmdWh | BCR | actVal | ST
MEAS_VAL | Electrical storage | Reactive energy demand (direction: from busbar). | integer | VArh | R | change & integrity | STO |  | MMTR | DmdVArh | BCR | actVal | ST
SCHD_INFO | Electrical storage | PV active power forecast schedule provider | character | / | R | Initial | STO | STOCTL_ | FSCH | NamPlt | LPL | vendor | DC
SCHD_INFO | Electrical storage | PV active power forecast schedule revision | character | / | R | Initial | STO | STOCTL_ | FSCH | NamPlt | LPL | swRev | DC
SCHD_INFO | Electrical storage | PV active power forecast schedule description | character | / | R | Initial | STO | STOCTL_ | FSCH | NamPlt | LPL | d | DC
SCHD_INFO | Electrical storage | A placeholder for later use | character | / | R | Initial | STO | STOCTL_ | FSCH | NamPlt | LPL | configRev | DC
SCHD_INFO | Electrical storage | State of this schedule | enumeration | / | R | change | STO | STOCTL_ | FSCH | SchdSt | ENS | stVal | ST | ScheduleStateKind
SCHD_INFO | Electrical storage | The current schedule entry of a running schedule. This is the Data-Instance-ID of the data object ValXXX (e.g. ValASG). As long as the schedule is not running the value shall be 0. | integer | / | R | change | STO | STOCTL_ | FSCH | SchdEntr | INS | stVal | ST
SCHD_INFO | Electrical storage | The time when the schedule started running. If the schedule is not running, the quality of the value is set to invalid. | timestamp | / | R | change | STO | STOCTL_ | FSCH | ActStrTm | TCS | stVal | ST
SCHD_INFO | Electrical storage | The next time when the schedule is planned/intented to start or re-start running. If no schedules are planned running, the quality of the value is set to invalid. | timestamp | / | R | change | STO | STOCTL_ | FSCH | NxtStrTm | TCS | stVal | ST
SCHD_INFO | Electrical storage | Enumeration reflecting the potential error which has happened at the latest Schedule Enabling request | enumeration | / | R | change | STO | STOCTL_ | FSCH | SchdEnaErr | ENS | stVal | ST | ScheduleEnablingErrorKind
SCHD_INFO | Electrical storage | Current value determined by the schedule. As long as the schedule is not running the quality of the value is invalid. The unit of this data shall be the same as the unit of the data object(s) ValASG | float | / | R | change | STO | STOCTL_ | FSCH | ValMV | MV | mag | MX
SCHD_INFO | Electrical storage | (controllable) Operating with value true initiates enable transition request according to the state diagram; operating with value false is ignored. The change of its status value is a local issue. | boolean | / | R/W | change | STO | STOCTL_ | FSCH | EnaReq | SPC | ctlVal
SCHD_INFO | Electrical storage | (controllable) Operating with value true initiates disable transition request according to the state diagram; operating with value false is ignored. The change of its status value is a local issue. | boolean | / | R/W | change | STO | STOCTL_ | FSCH | DsaReq | SPC | ctlVal
SCHD_INFO | Electrical storage | The priority relation of this schedule (0..n) with higher numbers superseding lower numbers. Shall be a positive value. If missing the default is zero. | unsigned integer | / | R/W | change | STO | STOCTL_ | FSCH | SchdPrio | ING | setVal | SP
SCHD_INFO | Electrical storage | The number of schedule entries that are valid out of the instantiated ValASG, ValING, ValSPG or ValENG. NumEntr shall be > 0. NumEntr is <= number of instantiated Val[ASG¦ING¦SPG¦ENG]'s | unsigned integer | / | R/W | change | STO | STOCTL_ | FSCH | NumEntr | ING | setVal | SP
SCHD_INFO | Electrical storage | The schedule interval duration in time entities as specified in the unit. The SIUnit is mandatory in this data object. The total duration of a schedule shall be (NumEntr x SchdIntv). | unsigned integer | s | R/W | change | STO | STOCTL_ | FSCH | SchdIntv | ING | setVal | SP
SCHD_INFO | Electrical storage | The ASG scheduled values (current value output as MV). Multiple entries should be possible. | float | / | R/W | change | STO | STOCTL_ | FSCH | ValASG | ASG | setMag | SP
SCHD_INFO | Electrical storage | Start time of the schedule in UTC time. | timestamp | / | R/W | change | STO | STOCTL_ | FSCH | StrTm | TSG | setTm | SP
SCHD_INFO | Electrical storage | If true, the change of the schedule to the running and activated state is triggered by an external event and not by the start time. The external event is referenced through 'InSyn'. | boolean | / | R/W | change | STO | STOCTL_ | FSCH | EvtTrg | SPG | setVal | SP
SCHD_INFO | Electrical storage | Object reference of the external trigger if the schedule is triggered by an event. | objectReference | / | R/W | change | STO | STOCTL_ | FSCH | InSyn | ORG | setSrcRef | SP
SCHD_INFO | Electrical storage | If true, once terminated or disabled, the schedule will change to the validated state, otherwise it will change to the not ready state. | boolean | / | R/W | change | STO | STOCTL_ | FSCH | SchdReuse | SPG | setVal | SP
SCHD_INFO | Electrical storage | Object reference of data object bound to the input n. | objectReference | / | R/W | change | STO | STOCTL_ | FSCH | InRef | ORG | setSrcRef | SP
SCHD_INFO | Electrical storage | PV active power forecast schedule controller manager | character | / | R | Initial | STO | STOCTL_ | FSCC | NamPlt | LPL | vendor | DC
SCHD_INFO | Electrical storage | PV active power forecast schedule controller revision | character | / | R | Initial | STO | STOCTL_ | FSCC | NamPlt | LPL | swRev | DC
SCHD_INFO | Electrical storage | PV active power forecast schedule controller description | character | / | R | Initial | STO | STOCTL_ | FSCC | NamPlt | LPL | d | DC
SCHD_INFO | Electrical storage | A placeholder for later use | character | / | R | Initial | STO | STOCTL_ | FSCC | NamPlt | LPL | configRev | DC
SCHD_INFO | Electrical storage | Indication of which schedule is active as an object reference. As long as no schedule is active the quality of the value is invalid. The active schedule is selected by the schedule controller within the running schedules based on the priority of the running schedules. | objectReference | / | R | change | STO | STOCTL_ | FSCC | ActSchdRef | ORS | stVal | ST
SCHD_INFO | Electrical storage | Current value determined by the schedule. As long as the schedule is not running the quality of the value shall be set to invalid. The unit of this data shall be the same as the unit of the data object(s) FSCH.ValASG. | float | W | R | change | STO | STOCTL_ | FSCC | ValMV | MV | mag | MX
SCHD_INFO | Electrical storage | Object reference to the entity controlled by the schedule. | objectReference | / | R/W | change | STO | STOCTL_ | FSCC | CtlEnt | ORG | setSrcRef | SP
SCHD_INFO | Electrical storage | Object reference of schedule n (an LN reference to the LN of class FSCH). | objectReference | / | R/W | change | STO | STOCTL_ | FSCC | Schd | ORG | setSrcRef | SP
SCHD_INFO | Electrical storage | Object reference of data object bound to the input n. | objectReference | / | R/W | change | STO | STOCTL_ | FSCC | InRef | ORG | setSrcRef | SP
SW_META | ECP | Name plate of the logical node | character | / | R | Initial | LOAD |  | LLN0 | NamPlt | LPL | vendor | DC
SW_META | ECP | Name plate of the logical node | character | / | R | Initial | LOAD |  | LLN0 | NamPlt | LPL | swRev | DC
SW_META | ECP | Name plate of the logical node | character | / | R | Initial | LOAD |  | LLN0 | NamPlt | LPL | d | DC
SW_META | ECP | A placeholder for later use | character | / | R | Initial | LOAD |  | LLN0 | NamPlt | LPL | configRev | DC
STAT_INFO | ECP | ECP data service failure description | character | / | R | Change | LOAD |  | LLN0 | Beh | ENS | d | DC
SW_META | ECP | ECP service provider | character | / | R | Initial | LOAD |  | DECP | NamPlt | LPL | vendor | DC
SW_META | ECP | ECP service software version | character | / | R | Initial | LOAD |  | DECP | NamPlt | LPL | swRev | DC
SW_META | ECP | ECP service description | character | / | R | Initial | LOAD |  | DECP | NamPlt | LPL | d | DC
SW_META | ECP | A placeholder for later use | character | / | R | Initial | LOAD |  | DECP | NamPlt | LPL | configRev | DC
STAT_INFO | ECP | Type of circuit phases | enumeration | / | R | Initial | LOAD |  | DECP | PhsConnTyp | ENS | stVal | ST | PhaseKind
SETTING | ECP | Default reference voltage for functions using voltage at this ECP as input | float | V | R/W | change | LOAD |  | DECP | VRef | ASG | setMag | SP
SETTING | ECP | Percent of VRef to use in calculating the voltage to use in operational function calculations | float | % | R/W | change | LOAD |  | DECP | VRefPct | ASG | setMag | SP
SETTING | ECP | Electrical active power rating at ECP | float | W | R/W | change | LOAD |  | DECP | WRtg | ASG | setMag | SP
SETTING | ECP | Reactive power rating at ECP | float | Var | R/W | change | LOAD |  | DECP | VArRtg | ASG | setMag | SP
SETTING | ECP | Apparent power rating at ECP | float | VA | R/W | change | LOAD |  | DECP | VARtg | ASG | setMag | SP
SETTING | ECP | Voltage rating at ECP | float | V | R/W | change | LOAD |  | DECP | VRtg | ASG | setMag | SP
SETTING | ECP | Nominal frequency at ECP | float | Hz | R/W | change | LOAD |  | DECP | HzNom | ASG | setMag | SP
SETTING | ECP | Rated maximum voltage | float | V | R/W | change | LOAD |  | DECP | VMax | ASG | setMag | SP
SETTING | ECP | Rated minimum voltage | float | V | R/W | change | LOAD |  | DECP | Vmin | ASG | setMag | SP
CTRL_PARA | ECP | Identity of electrical reference point as a Visible String | character | / | R/W | change | LOAD |  | DECP | ElcRefId | VSG | setVal | SP
CTRL_PARA | ECP | Indication whether the active power from the DER referencing this ECP is included in the measurements coming from the ECP. This is important for managing Generation and Load Following, as well as Peak Power Limiting functions. | boolean | / | R | change | LOAD |  | DECP | DERMsIncl | SPG | setVal | SP
HW_META | Load | Storage system name | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | name | DC
HW_META | Load | Storage system hardware vendor | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | vendor | DC
HW_META | Load | Storage system hardware model | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | model | DC
HW_META | Load | Storage system hardware serial number | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | serNum | DC
SW_META | Load | Storage system software revision | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | swRev | DC
HW_META | Load | Storage system owner | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | owner | DC
HW_META | Load | Storage system connected electrical power system | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | ePSName | DC
HW_META | Load | Storage system primary operator | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | primeOper | DC
HW_META | Load | Storage system secondary operator | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | secondOper | DC
STAT_INFO | Load | Storage system hardware reversion | character | / | R | Change | LOAD |  | DLOD | EEName | DPL | hwRev | DC
STAT_INFO | Load | Storage system hardware UUID | character | / | R | Initial | LOAD |  | DLOD | EEName | DPL | mRID | DC
STAT_INFO | Load | Storage system hardware description | character | / | R | Change | LOAD |  | DLOD | EEName | DPL | d | DC
STAT_INFO | Load | Name plate of the logical node | character | / | R | Initial | LOAD |  | DLOD | NamPlt | LPL | vendor | DC
STAT_INFO | Load | Name plate of the logical node | character | / | R | Initial | LOAD |  | DLOD | NamPlt | LPL | swRev | DC
STAT_INFO | Load | Name plate of the logical node | character | / | R | Initial | LOAD |  | DLOD | NamPlt | LPL | d | DC
STAT_INFO | Load | A placeholder for later use | character | / | R | Initial | LOAD |  | DLOD | NamPlt | LPL | configRev | DC
STAT_INFO | Load | Current state of operation of the distributed energy resource. | enumeration | / | R | change & integrity | LOAD |  | DLOD | DEROpSt | ENS | stVal | ST | DERStateKind
STAT_INFO | Load | State of external (electrical, mechanical or communication) equipment to which the logical node is associated. | enumeration | / | R | change | LOAD |  | DLOD | EEHealth | ENS | stVal | ST | HealthKind
STAT_INFO | Load | Operation time of the external (electrical, mechanical or communication) equipment since start of the operation. | unsigned integer | h |  | integrity | LOAD |  | DLOD | OpTmh | INS | stVal | ST
MEAS_VAL | Load | The total amount of reactive power available for absorbing even if possibly impacting active power output (the use of this DO is mutually exclusive with the use of VArTot) | float | VAr | R | change & integrity | LOAD |  | DLOD | AvarTot | MV | mag | MX
MEAS_VAL | Load | The total amount of reactive power available for injecting even if possibly impacting active power output (the use of this DO is mutually exclusive with the use of VArTot) | float | VAr | R | change & integrity | LOAD |  | DLOD | IvarTot | MV | mag | MX
FLEX_INFO | Load | The amount of reactive power available without impacting active power output if the distinction between absorbing and injecting reactive power is not significant (the use of this DO is mutually exclusive with the use of AvarAvl and IvarAvl) | float | VAr | R | change & integrity | LOAD |  | DLOD | VArAvl | MV | mag | MX
FLEX_INFO | Load | The amount of reactive power available for absorbing without impacting active power output (the use of this DO is mutually exclusive with the use of VArAvl) | float | VAr | R | change & integrity | LOAD |  | DLOD | AvarAvl | MV | mag | MX
FLEX_INFO | Load | The amount of reactive power available for injecting without impacting active power output (the use of this DO is mutually exclusive with the use of VArAvl) | float | VAr | R | change & integrity | LOAD |  | DLOD | IvarAvl | MV | mag | MX
MEAS_VAL | Load | Actual self service energy used | float | Wh | R | change & integrity | LOAD |  | DLOD | SelfSvcWh | MV | mag | MX
MEAS_VAL | Load | Actual percentage of apparent power output based on VAMax | float | % | R | change & integrity | LOAD |  | DLOD | VAPct | MV | mag | MX
FLEX_INFO | Load | Available capability (measured or calculated) for increasing active output, including increasing generation of active power, even if currently consuming power. | float | W | R | change & integrity | LOAD |  | DLOD | AvlUpW | MV | mag | MX
FLEX_INFO | Load | Available capability (measured or calculated) for decreasing active power, including increasing the consumption of active power, even if currently generating power. | float | W | R | change & integrity | LOAD |  | DLOD | AvlDnW | MV | mag | MX
CTRL_PARA | Load | (controllable) Operating with the value expressed in ctlVal (selected among the list specified in DERStateControlKind) initiates the appropriate transition request. The reading of its attribute stVal is meaningless. The resulting state of the DER shall be observed in the DEROpSt DO. | enumeration | / | W | change | LOAD |  | DLOD | DEROpStCtl | ENC | ctlVal | MX | DERStateTransitionKi nd
CTRL_PARA | Load | Active power setpoint. | float | W | W | change | LOAD |  | DLOD | WSpt | APC | ctlVal
CTRL_PARA | Load | Active power setpoint that is requested. | float | W | R | change & integrity | LOAD |  | DLOD | WSpt | APC | mxVal | MX
CTRL_PARA | Load | Reactive power setpoint. | float | VAr | W | change | LOAD |  | DLOD | VArSpt | APC | ctlVal
CTRL_PARA | Load | Reactive power setpoint that is requested. | float | VAr | R | change & integrity | LOAD |  | DLOD | VArSpt | APC | mxVal | MX
CTRL_PARA | Load | (controllable) Operations count, can be reset to a value different than 0. | unsigned integer | / | R/W | change | LOAD |  | DLOD | OpCntRs | INC | ctlVal
SETTING | Load | Nameplate maximum Load active power rating at unity power factor | float | W | R/W | change | LOAD |  | DLOD | WMaxRtg | ASG | setMag | SP
SETTING | Load | Maximum voltage rating | float | V | R/W | change | LOAD |  | DLOD | VMaxRtg | ASG | setMag | SP
SETTING | Load | Minimum voltage rating | float | V | R/W | change | LOAD |  | DLOD | VMinRtg | ASG | setMag | SP
SETTING | Load | Maximum current rating under nominal voltage under nominal power factor while charging | float | A | R/W | change | LOAD |  | DLOD | AMaxRtg | ASG | setMag | SP
SETTING | Load | Nameplate maximum apparent charging power rating | float | VA | R/W | change | LOAD |  | DLOD | VAMaxRtg | ASG | setMag | SP
SETTING | Load | Maximum nameplate charging ramp up rating | float | W | R/W | change | LOAD |  | DLOD | WRpuMaxRtg | ASG | setMag | SP
SETTING | Load | Maximum nameplate charging ramp down rating | float | W | R/W | change | LOAD |  | DLOD | WRpdMaxRtg | ASG | setMag | SP
SETTING | Load | Maximum nameplate charging ramp down rating | float | W | R/W | change | LOAD |  | DLOD | WMax | ASG | setMag | SP
SETTING | Load | Default ramp rate for changes in active power: percentage of WMax per second | float | W | R/W | change | LOAD |  | DLOD | WRmp | ASG | setMag | SP
SETTING | Load | Setting for maximum absorbing reactive power (the use of this DO is mutually exclusive with the use of VArMax) | float | VAr | R/W | change | LOAD |  | DLOD | AvarMax | ASG | setMag | SP
SETTING | Load | Setting for maximum supply (injection) reactive power (the use of this DO is mutually exclusive with the use of VArMax) | float | VAr | R/W | change | LOAD |  | DLOD | IvarMax | ASG | setMag | SP
SETTING | Load | Setting for maximum voltage operational rating | float | V | R/W | change | LOAD |  | DLOD | VMax | ASG | setMag | SP
SETTING | Load | Setting for minimum voltage operational rating | float | V | R/W | change | LOAD |  | DLOD | VMin | ASG | setMag | SP
SETTING | Load | Setting for maximum operational current rating under nominal voltage under nominal power factor | float | A | R/W | change | LOAD |  | DLOD | AMax | ASG | setMag | SP
SETTING | Load | Setting for maximum absorbing apparent power (the use of this DO is mutually exclusive with the use of VAMax) | float | VA | R/W | change | LOAD |  | DLOD | AvaMax | ASG | setMag | SP
SETTING | Load | Setting for maximum injecting apparent power (the use of this DO is mutually exclusive with the use of VAMax) | float | VA | R/W | change | LOAD |  | DLOD | IvaMax | ASG | setMag | SP
SETTING | Load | Reference for reactive power setpoints. Selects which setpoint is active. | float | / | R/W | change | LOAD |  | DLOD | VArSptRef | ENG | setMag | SP | ReactivePowerRefPar amKind
SETTING | Load | Connection type of ECP: connection to DER (Point of Connection (PoC)), to load, within Local Electric Power System (Local EPS), Point of Common Coupling (PCC), or directly to Area EPS | enumeration | / | R/W | change | LOAD |  | DLOD | EcpConnTyp | ENG | setVal | SP | ECPConnKind
SETTING | Load | Phase type of electrical connection of the DER | enumeration | / | R/W | change | LOAD |  | DLOD | PhsConnTyp | ENG | setVal | SP | PhaseKind
SETTING | Load | Type of DER | enumeration | / | R/W | change | LOAD |  | DLOD | DERTyp | ENG | setVal | SP | DERUnitKind
SETTING | Load | Maximum temperature rating | float | °C | R/W | change | LOAD |  | DLOD | TmpMaxRtg | ASG | setMag | SP
SETTING | Load | Exposure to fault rates as percent of ?? | float | % | R/W | change | LOAD |  | DLOD | FltRtgPct | ASG | setMag | SP
SETTING | Load | Max fault current rating | float | A | R/W | change | LOAD |  | DLOD | FltAMaxRtg | ASG | setMag | SP
SETTING | Load | Selfservice voltage | float | V | R/W | change | LOAD |  | DLOD | SelfVRtg | ASG | setMag | SP
SETTING | Load | Max fault duration rating | float | ms | R/W | change | LOAD |  | DLOD | FltDurMaxTms | ASG | setMag | SP
SETTING | Load | Selfservice nominal power | float | W | R/W | change | LOAD |  | DLOD | SelfWRtg | ASG | setMag | SP
SETTING | Load | Selfservice nominal power factor | float | / | R/W | change | LOAD |  | DLOD | SelfPFRtg | ASG | setMag | SP
SETTING | Load | Selfservice acceptable voltage range | float | V | R/W | change | LOAD |  | DLOD | SelfVRngRtg | ASG | setMag | SP
SETTING | Load | Efficiency at rated capacity as percent | float | % | R/W | change | LOAD |  | DLOD | EfcRtgPct | ASG | setMag | SP
SETTING | Load | Rated Nominal frequency of usage of the DER | float | Hz | R/W | change | LOAD |  | DLOD | HzNomRtg | ASG | setMag | SP
SETTING | Load | Rated minimal frequency of usage of the DER | float | Hz | R/W | change | LOAD |  | DLOD | HzMinRtg | ASG | setMag | SP
SETTING | Load | Rated maximum frequency of usage of the DER | float | Hz | R/W | change | LOAD |  | DLOD | HzMaxRtg | ASG | setMag | SP
SETTING | Load | Internal identifier of the resource within a system which is using that resource. It complements the mRID defined as part of the EEname DO. Different DERIds may be defined for different system users. | float | / | R/W | change | LOAD |  | DLOD | DERId | ASG | setMag | SP
FLEX_INFO | Load | A list of energy market partner ID | character | / |  | Initial | LOAD |  | DCCT | NamPlt | LPL | vendor | DC
FLEX_INFO | Load | A list of energy purchaser priority | character | / |  | Initial | LOAD |  | DCCT | NamPlt | LPL | swRev | DC
FLEX_INFO | Load | Registered energy platform | character | / |  | Initial | LOAD |  | DCCT | NamPlt | LPL | d | DC
FLEX_INFO | Load | Currently activated energy purchaser | character | / |  | Initial | LOAD |  | DCCT | NamPlt | LPL | configRev | DC
FLEX_INFO | Load | ISO 4217 currency 3-character code | character | / |  | change | LOAD |  | DCCT | Ccy | CUG | cur | SP
FLEX_INFO | Load | Marginal operational cost per hour | float | cur |  | change | LOAD |  | DCCT | OpCost | ASG | setMag | SP
FLEX_INFO | Load | Marginal operational cost per kWh | float | cur |  | change | LOAD |  | DCCT | OpWhCost | ASG | setMag | SP
FLEX_INFO | Load | Cost to start up DER | float | cur |  | change | LOAD |  | DCCT | StrCost | ASG | setMag | SP
FLEX_INFO | Load | Cost to stop DER | float | cur |  | change | LOAD |  | DCCT | StopCost | ASG | setMag | SP
FLEX_INFO | Load | Cost to ramp DER per kW per minute | float | cur |  | change | LOAD |  | DCCT | RampCost | ASG | setMag | SP
FLEX_INFO | Load | Incremental heat rate piecewise linear curve costs. | Curve | / |  | change | LOAD |  | DCCT | HeatRteCost | CSG
FLEX_INFO | Load | Incremental carbon emission curve costs. | Curve | / |  | change | LOAD |  | DCCT | CRteCost | CSG
MKT_IF | Load | Name plate of the logical node. | character | / |  | Initial | LOAD |  | DCST | NamPlt | LPL | vendor | DC
MKT_IF | Load | Name plate of the logical node. | character | / |  | Initial | LOAD |  | DCST | NamPlt | LPL | swRev | DC
MKT_IF | Load | Name plate of the logical node. | character | / |  | Initial | LOAD |  | DCST | NamPlt | LPL | d | DC
MKT_IF | Load | Name plate of the logical node. | character | / |  | Initial | LOAD |  | DCST | NamPlt | LPL | configRev | DC
MKT_IF | Load | ISO 4217 currency 3-character code | character | / |  | change | LOAD |  | DCST | Ccy | CUG | cur | SP
MKT_IF | Load | Cost to start up DER | float | cur |  | change | LOAD |  | DCST | StrCost | ASG | setMag | SP
MKT_IF | Load | Cost to stop DER | float | cur |  | change | LOAD |  | DCST | StopCost | ASG | setMag | SP
MKT_IF | Load | Cost to ramp DER per kW per minute | float | cur |  | change | LOAD |  | DCST | RampCost | ASG | setMag | SP
MKT_IF | Load | Incremental carbon emission curve costs. | Curve | / |  | change | LOAD |  | DCST | CRteCost | CSG
MKT_IF | Load | Active curve characteristics for the incremental heat rate curve | Curve | / |  | change | LOAD |  | DCST | HeatRteAct | CSG
MKT_IF | Load | Incremental heat rate piecewise linear curve costs. | Curve | / |  | change | LOAD |  | DCST | HeatRteCost | CSG
HW_META | Load | measuring unit vendor | character | / | R | Initial | LOAD |  | MMXU | NamPlt | LPL | vendor | DC
HW_META | Load | measuring unit software version | character | / | R | Initial | LOAD |  | MMXU | NamPlt | LPL | swRev | DC
HW_META | Load | measuring unit description | character | / | R | Initial | LOAD |  | MMXU | NamPlt | LPL | d | DC
HW_META | Load | A placeholder for later use | character | / | R | Initial | LOAD |  | MMXU | NamPlt | LPL | configRev | DC
STAT_INFO | Load | status of the power vector expressed through one of the 9 zones of the PQ diagram quadrant, based on the signing conventions set with PFSign and PFExt. | enumeration | / | R | change | LOAD |  | MMXU | PQSt | ENS | stVal | ST | QuadrantRunningStateKind
MEAS_VAL | Load | total active power measurement | float | W | R | change & integrity | LOAD |  | MMXU | TotW | MV | mag | MX
MEAS_VAL | Load | total reactive power measurement | float | Var | R | change & integrity | LOAD |  | MMXU | TotVar | MV | mag | MX
MEAS_VAL | Load | total apparent power measurement | float | VA | R | change & integrity | LOAD |  | MMXU | TotVA | MV | mag | MX
MEAS_VAL | Load | ratio of the absolute active power to the apparent power | float | / | R | change & integrity | LOAD |  | MMXU | TotPF | MV | mag | MX
MEAS_VAL | Load | frequency | float | Hz | R | change & integrity | LOAD |  | MMXU | Hz | MV | mag | MX
MEAS_VAL | Load | Phase to phase voltages. | float | V | R | change & integrity | LOAD |  | MMXU | PPV | DEL | phsAB/BC/CA.cVal.mag | MX
MEAS_VAL | Load | Phase to neutral voltages. | float | V | R | change & integrity | LOAD |  | MMXU | PNV | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Load | Phase to ground (line) voltages. | float | V | R | change & integrity | LOAD |  | MMXU | PhV | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Load | Phase to ground/phase to neutral three phase currents. | float | A | R | change & integrity | LOAD |  | MMXU | A | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Load | Phase to ground/phase to neutral real powers P. | float | W | R | change & integrity | LOAD |  | MMXU | W | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Load | Phase to ground/phase to neutral reactive powers Q. | float | Var | R | change & integrity | LOAD |  | MMXU | VAr | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Load | Phase to ground/phase to neutral apparent powers S. | float | VA | R | change & integrity | LOAD |  | MMXU | VA | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Load | Phase to ground/phase to neutral signed power factors. | float | / | R | change & integrity | LOAD |  | MMXU | PF | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Load | Phase to ground/phase to neutral impedances in a three-phase system. | float | ohm | R | change & integrity | LOAD |  | MMXU | Z | WYE | phsA/B/C.cVal.mag | MX
MEAS_VAL | Load | Rate of change of frequency | float | Hz/s | R | change & integrity | LOAD |  | MMXU | HzRte | MV | mag | MX
MEAS_VAL | Load | Arithmetic average of the magnitude of current of the 3 phases: average(Ia,Ib,Ic). | float | A | R | change & integrity | LOAD |  | MMXU | AvAPhs | MV | mag | MX
MEAS_VAL | Load | Arithmetic average of the magnitude of phase to phase voltage of the 3 phases: average(PPVa, PPVb, PPVc). | float | V | R | change & integrity | LOAD |  | MMXU | AvPPVPhs | MV | mag | MX
MEAS_VAL | Load | Arithmetic average of the magnitude of phase to reference voltage of the 3 phases: average(PhVa, PhVb, PhVc). | float | V | R | change & integrity | LOAD |  | MMXU | AvPhVPhs | MV | mag | MX
MEAS_VAL | Load | Arithmetic average of the magnitude of active power of the 3 phases: average(Wa, Wb, Wc). | float | W | R | change & integrity | LOAD |  | MMXU | AvWPhs | MV | mag | MX
MEAS_VAL | Load | Arithmetic average of the magnitude of apparent power of the 3 phases: average(VAa, VAb, VAc). | float | Var | R | change & integrity | LOAD |  | MMXU | AvVAPhs | MV | mag | MX
MEAS_VAL | Load | Arithmetic average of the magnitude of reactive power of the 3 phases: average(VAra, VArb, VArc). | float | VA | R | change & integrity | LOAD |  | MMXU | AvVArPhs | MV | mag | MX
MEAS_VAL | Load | Arithmetic average of the magnitude of power factor of the 3 phases: average(PFa, PFb, PFc). | float | / | R | change & integrity | LOAD |  | MMXU | AvPFPhs | MV | mag | MX
MEAS_VAL | Load | Arithmetic average of the magnitude of impedance of the 3 phases: average(Za, Zb, Zc). | float | ohm | R | change & integrity | LOAD |  | MMXU | AvZPhs | MV | mag | MX
MEAS_VAL | Load | meter vendor | character | / | R | Initial | LOAD |  | MMTR | NamPlt | LPL | vendor | DC
MEAS_VAL | Load | meter software version | character | / | R | Initial | LOAD |  | MMTR | NamPlt | LPL | swRev | DC
MEAS_VAL | Load | meter description | character | / | R | Initial | LOAD |  | MMTR | NamPlt | LPL | d | DC
MEAS_VAL | Load | meter configuration revision | character | / | R | Initial | LOAD |  | MMTR | NamPlt | LPL | configRev | DC
MEAS_VAL | Load | Net apparent energy since last reset. | integer | VAh | R | change & integrity | LOAD |  | MMTR | TotVAh | BCR | actVal | ST
MEAS_VAL | Load | Net real energy since last reset. | integer | Wh | R | change & integrity | LOAD |  | MMTR | TotWh | BCR | actVal | ST
MEAS_VAL | Load | Net reactive energy since last reset. | integer | VArh | R | change & integrity | LOAD |  | MMTR | TotVArh | BCR | actVal | ST
MEAS_VAL | Load | Real energy supply (default direction: towards busbar). | integer | Wh | R | change & integrity | LOAD |  | MMTR | SupWh | BCR | actVal | ST
MEAS_VAL | Load | Reactive energy supply (default direction: towards busbar). | integer | VArh | R | change & integrity | LOAD |  | MMTR | SupVArh | BCR | actVal | ST
MEAS_VAL | Load | Real energy demand (direction: from busbar). | integer | Wh | R | change & integrity | LOAD |  | MMTR | DmdWh | BCR | actVal | ST
MEAS_VAL | Load | Reactive energy demand (direction: from busbar). | integer | VArh | R | change & integrity | LOAD |  | MMTR | DmdVArh | BCR | actVal | ST
SW_META | data interface | Meteorological data provider | character | / | R | Initial | METEO |  | LLN0 | NamPlt | LPL | vendor | DC
SW_META | data interface | Meteorological data version | character | / | R | Initial | METEO |  | LLN0 | NamPlt | LPL | swRev | DC
SW_META | data interface | Meteorological datadescription | character | / | R | Initial | METEO |  | LLN0 | NamPlt | LPL | d | DC
SW_META | data interface | A placeholder for later use | character | / | R | Initial | METEO |  | LLN0 | NamPlt | LPL | configRev | DC
STAT_INFO | data interface | Meteorological data failure description | character | / | R | Change | METEO |  | LLN0 | Beh | ENS | d | DC
HW_META | data interface | Weather-station (if locally installed) name | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | name | DC
HW_META | data interface | Weather-station (if locally installed) hardware vendor | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | vendor | DC
HW_META | data interface | Weather-station (if locally installed) hardware model | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | model | DC
HW_META | data interface | Weather-station (if locally installed) hardware serial number | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | serNum | DC
SW_META | data interface | Weather-station (if locally installed) software revision | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | swRev | DC
HW_META | data interface | Weather-station (if locally installed) location | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | location | DC
HW_META | data interface | Weather-station (if locally installed) longitude, WGS84 coordinates | float | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | longitude | DC
HW_META | data interface | Weather-station (if locally installed) altitude, WGS84 coordinates | float | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | altitude | DC
HW_META | data interface | Weather-station (if locally installed) owner | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | owner | DC
HW_META | data interface | Weather-station (if locally installed) connected electrical power system | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | ePSName | DC
HW_META | data interface | Weather-station (if locally installed) primary operator | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | primeOper | DC
HW_META | data interface | Weather-station (if locally installed) secondary operator | character | / | R | Initial | METEO |  | LPHD | PhyNam | DPL | secondOper | DC
STAT_INFO | data interface | Weather-station (if locally installed) hardware reversion | character | / | R | Change | METEO |  | LPHD | PhyNam | DPL | hwRev | DC
STAT_INFO | data interface | Weather-station (if locally installed) hardware failure description | character | / | R | Change | METEO |  | LPHD | Beh | ENS | d | DC
HW_META | data interface | vendor of meteorological sensor | character | / | R | Initial | METEO |  | MMET | NamPlt | LPL | vendor | DC
SW_META | data interface | Software revision of meteorological sensor | character | / | R | Initial | METEO |  | MMET | NamPlt | LPL | swRev | DC
HW_META | data interface | Type of meteorological sensor and its classification (A, B or C) acc. to ISO 9060 - OPTIONAL | character | / | R | Initial | METEO |  | MMET | NamPlt | LPL | d | DC
HW_META | data interface | A placeholder for later use | character | / | R | Initial | METEO |  | MMET | NamPlt | LPL | configRev | DC
METEO_INFO | data interface | Total horizontal insolation - if it is available and reliable (MMET, Data object name: HorInsol) - OPTIONAL | float | W/m2 | R | change & integrity | METEO |  | MMET | HorInsol | MV | mag | MX
METEO_INFO | data interface | Direct normal insolation - if it is available and reliable (MMET, Data object name: DctInsol) - OPTIONAL | float | W/m2 | R | change & integrity | METEO |  | MMET | DctInsol | MV | mag | MX
METEO_INFO | data interface | Diffuse insolation - if it is available and reliable (MMET, Data object name: DffInsol) - OPTIONAL | float | W/m2 | R | change & integrity | METEO |  | MMET | DffInsol | MV | mag | MX
METEO_INFO | data interface | Ambient temperature - if it is available and reliable (MMET, Data object name: EnvTmp) - OPTIONAL | float | °C | R | change & integrity | METEO |  | MMET | EnvTmp | MV | mag | MX
METEO_INFO | data interface | Snowfall - if it is available and reliable (MMET, Data object name: SnwFll) - OPTIONAL | float | kg/m2 | R | change & integrity | METEO |  | MMET | SnwFll | MV | mag | MX
METEO_INFO | data interface | Snow cover - if it is available and reliable (MMET, Data object name: SnwCvr) - OPTIONAL | float | kg/m2 | R | change & integrity | METEO |  | MMET | SnwCvr | MV | mag | MX
METEO_INFO | data interface | Rainfall - if it is available and reliable (MMET, Data object name: RnFll) - OPTIONAL | float | kg/m2 | R | change & integrity | METEO |  | MMET | RnFll | MV | mag | MX
METEO_INFO | data interface | Humidity - relative humidity - if it is available and reliable (MMET, Data object name: EnvHum) - OPTIONAL | float | % | R | change & integrity | METEO |  | MMET | EnvHum | MV | mag | MX
METEO_INFO | data interface | Barometric pressure - athmospheric pressure - if it is available and reliable (MMET, Data object name: EnvPres) - OPTIONAL | float | hPa | R | change & integrity | METEO |  | MMET | EnvPres | MV | mag | MX
METEO_INFO | data interface | Horizontal Wind direction - if it is available and reliable (MMET, Data object name: HorWdDir - OPTIONAL | float | deg. | R | change & integrity | METEO |  | MMET | HorWdDir | MV | mag | MX
METEO_INFO | data interface | Horizontal Wind speed - if it is available and reliable (MMET, Data object name: HorWdSpd) - OPTIONAL | float | m/s | R | change & integrity | METEO |  | MMET | HorWdSpd | MV | mag | MX
METEO_INFO | data interface | Plane of array insolation (insolation SIUnit [W/m2]). | float | W/m2 | R | change & integrity | METEO |  | MMET | PoaInsol | MV | mag | MX
METEO_INFO | data interface | Wet bulb temperature (typically in °C). | float | °C | R | change & integrity | METEO |  | MMET | WetBlbTmp | MV | mag | MX
METEO_INFO | data interface | Cloud cover level. | float | / | R | change & integrity | METEO |  | MMET | CloudCvr | MV | mag | MX
METEO_INFO | data interface | Dew point temperature | float | °C | R | change & integrity | METEO |  | MMET | DewPt | MV | mag | MX
METEO_INFO | data interface | Daylight duration (time elapsed between sunrise and sunset). | float | h | R | change & integrity | METEO |  | MMET | DlDur | MV | mag | MX
METEO_INFO | data interface | Average vertical wind speed. | float | m/s | R | change & integrity | METEO |  | MMET | VerWdDir | MV | mag | MX
METEO_INFO | data interface | Average vertical wind speed. | float | m/s | R | change & integrity | METEO |  | MMET | VerWdSpd | MV | mag | MX
METEO_INFO | data interface | Maximum wind gust speed. | float | m/s | R | change & integrity | METEO |  | MMET | WdGustSpd | MV | mag | MX
METEO_INFO | data interface | Snowfall density (typically in g/cm3 – density SIUnit [kg/m3]). | float | kg/m3 | R | change & integrity | METEO |  | MMET | SnwDen | MV | mag | MX
METEO_INFO | data interface | Snowfall temperature (typically in °C). | float | °C | R | change & integrity | METEO |  | MMET | SnwTmp | MV | mag | MX
|  | Water equivalent of snowfall (typically in mm – length SIUnit [m]). | float | m/s | R | change & integrity | METEO |  | MMET | SnwEq | MV | mag | MX
METEO_INFO | data interface | Global Tilted Irradiation - total radiation received on a surface with defined tilt and azimuth, fixed or sun-tracking. Is this parameter PoaInsol in MMET? | float | W/m2 | R/W | change & integrity | METEO
METEO_INFO | data interface | Pvout - estimated solar photovoltaic (PV) power generation. Representation as schedule. | float | W | R | change & integrity | METEO
SCHD_INFO | data interface | PV active power forecast schedule provider | character | / | R | Initial | METEO | PVGEN_ | FSCH | NamPlt | LPL | vendor | DC
SCHD_INFO | data interface | PV active power forecast schedule revision | character | / | R | Initial | METEO | PVGEN_ | FSCH | NamPlt | LPL | swRev | DC
SCHD_INFO | data interface | PV active power forecast schedule description | character | / | R | Initial | METEO | PVGEN_ | FSCH | NamPlt | LPL | d | DC
SCHD_INFO | data interface | A placeholder for later use | character | / | R | Initial | METEO | PVGEN_ | FSCH | NamPlt | LPL | configRev | DC
SCHD_INFO | data interface | State of this schedule | enumeration | / | R | change | METEO | PVGEN_ | FSCH | SchdSt | ENS | stVal | ST | ScheduleStateKind
SCHD_INFO | data interface | The current schedule entry of a running schedule. This is the Data-Instance-ID of the data object ValXXX (e.g. ValASG). As long as the schedule is not running the value shall be 0. | integer | / | R | change | METEO | PVGEN_ | FSCH | SchdEntr | INS | stVal | ST | ScheduleEnablingErrorKind
SCHD_INFO | data interface | The time when the schedule started running. If the schedule is not running, the quality of the value is set to invalid. | timestamp | / | R | change | METEO | PVGEN_ | FSCH | ActStrTm | TCS | stVal | ST
SCHD_INFO | data interface | The next time when the schedule is planned/intented to start or re-start running. If no schedules are planned running, the quality of the value is set to invalid. | timestamp | / | R | change | METEO | PVGEN_ | FSCH | NxtStrTm | TCS | stVal | ST
SCHD_INFO | data interface | Enumeration reflecting the potential error which has happened at the latest Schedule Enabling request | enumeration | / | R | change | METEO | PVGEN_ | FSCH | SchdEnaErr | ENS | stVal | ST | ScheduleEnablingErrorKind
SCHD_INFO | data interface | Current value determined by the schedule. As long as the schedule is not running the quality of the value is invalid. The unit of this data shall be the same as the unit of the data object(s) ValASG | float | / | R | change | METEO | PVGEN_ | FSCH | ValMV | MV | mag | MX
SCHD_INFO | data interface | (controllable) Operating with value true initiates enable transition request according to the state diagram; operating with value false is ignored. The change of its status value is a local issue. | boolean | / | R/W | change | METEO | PVGEN_ | FSCH | EnaReq | SPC | ctlVal
SCHD_INFO | data interface | (controllable) Operating with value true initiates disable transition request according to the state diagram; operating with value false is ignored. The change of its status value is a local issue. | boolean | / | R/W | change | METEO | PVGEN_ | FSCH | DsaReq | SPC | ctlVal
SCHD_INFO | data interface | The priority relation of this schedule (0..n) with higher numbers superseding lower numbers. Shall be a positive value. If missing the default is zero. | unsigned integer | / | R/W | change | METEO | PVGEN_ | FSCH | SchdPrio | ING | setVal | SP
SCHD_INFO | data interface | The number of schedule entries that are valid out of the instantiated ValASG, ValING, ValSPG or ValENG. NumEntr shall be > 0. NumEntr is <= number of instantiated Val[ASG¦ING¦SPG¦ENG]'s | unsigned integer | / | R/W | change | METEO | PVGEN_ | FSCH | NumEntr | ING | setVal | SP
SCHD_INFO | data interface | The schedule interval duration in time entities as specified in the unit. The SIUnit is mandatory in this data object. The total duration of a schedule shall be (NumEntr x SchdIntv). | unsigned integer | s | R/W | change | METEO | PVGEN_ | FSCH | SchdIntv | ING | setVal | SP
SCHD_INFO | data interface | The ASG scheduled values (current value output as MV). Multiple entries should be possible. | float | / | R/W | change | METEO | PVGEN_ | FSCH | ValASG | ASG | setMag | SP
SCHD_INFO | data interface | Start time of the schedule in UTC time. | timestamp | / | R/W | change | METEO | PVGEN_ | FSCH | StrTm | TSG | setTm | SP
SCHD_INFO | data interface | If true, the change of the schedule to the running and activated state is triggered by an external event and not by the start time. The external event is referenced through 'InSyn'. | boolean | / | R/W | change | METEO | PVGEN_ | FSCH | EvtTrg | SPG | setVal | SP
SCHD_INFO | data interface | Object reference of the external trigger if the schedule is triggered by an event. | objectReference | / | R/W | change | METEO | PVGEN_ | FSCH | InSyn | ORG | setSrcRef | SP
SCHD_INFO | data interface | If true, once terminated or disabled, the schedule will change to the validated state, otherwise it will change to the not ready state. | boolean | / | R/W | change | METEO | PVGEN_ | FSCH | SchdReuse | SPG | setVal | SP
SCHD_INFO | data interface | Object reference of data object bound to the input n. | objectReference | / | R/W | change | METEO | PVGEN_ | FSCH | InRef | ORG | setSrcRef | SP
SCHD_INFO | data interface | PV active power forecast schedule controller manager | character | / | R | Initial | METEO | PVGEN_ | FSCC | NamPlt | LPL | vendor | DC
SCHD_INFO | data interface | PV active power forecast schedule controller revision | character | / | R | Initial | METEO | PVGEN_ | FSCC | NamPlt | LPL | swRev | DC
SCHD_INFO | data interface | PV active power forecast schedule controller description | character | / | R | Initial | METEO | PVGEN_ | FSCC | NamPlt | LPL | d | DC
SCHD_INFO | data interface | A placeholder for later use | character | / | R | Initial | METEO | PVGEN_ | FSCC | NamPlt | LPL | configRev | DC
SCHD_INFO | data interface | Indication of which schedule is active as an object reference. As long as no schedule is active the quality of the value is invalid. The active schedule is selected by the schedule controller within the running schedules based on the priority of the running schedules. | objectReference | / | R | change | METEO | PVGEN_ | FSCC | ActSchdRef | ORS | stVal | ST
SCHD_INFO | data interface | Current value determined by the schedule. As long as the schedule is not running the quality of the value shall be set to invalid. The unit of this data shall be the same as the unit of the data object(s) FSCH.ValASG. | float | W | R | change | METEO | PVGEN_ | FSCC | ValMV | MV | mag | MX
SCHD_INFO | data interface | Object reference to the entity controlled by the schedule. | objectReference | / | R/W | change | METEO | PVGEN_ | FSCC | CtlEnt | ORG | setSrcRef | SP
SCHD_INFO | data interface | Object reference of schedule n (an LN reference to the LN of class FSCH). | objectReference | / | R/W | change | METEO | PVGEN_ | FSCC | Schd | ORG | setSrcRef | SP
SCHD_INFO | data interface | Object reference of data object bound to the input n. | objectReference | / | R/W | change | METEO | PVGEN_ | FSCC | InRef | ORG | setSrcRef | SP